Engine Circular No. 25

| NO: ENG/MMAM-37(6)/99 | Dated: April 12, 2004 |
| --- | --- |
| Sub: Guidelines for the maintenance & inspection of Fire-Protection systems and appliance. |  |
| Sir, Recognizing the importance of proper maintenance and inspection of fire-protection systems and appliances, Guidelines as per MSC/Cir.850 for the maintenance and inspection of fire-protection systems and appliances are enclosed. This circular provides for guidance with regard to periodical maintenance, testing and inspection of fire fighting systems and appliances. This may please be circulated to all concerned. The circular is available on the website of the Directorate: www.dgshipping.com This issues with the approval of the Chief Surveyor with the Government of India. Yours faithfully, Sd/-(D.Mehrotra) Engineer and Ship Surveyor Encl : As above. |  |
| Guidelines for the maintenance and inspection of Fire-Protection systems and appliances. 1. Application These Guidelines apply to all ships; however it does not contain an exhaustive list of maintenance items and should be used as a recommendation only. 2. Operational readiness All fire protection systems and appliances should at all times be in good order and available for immediate use while the ship is in service. If a fire protection system is under repair, then suitable arrangements should be made to ensure safety is not diminished. 3. Maintenance and testing Instructions for on-board maintenance, not necessarily by the ship’s crew, and testing of active and passive fire protection systems and appliances should be easily understood, illustrated wherever possible, and, as appropriate, should include the following for each system or appliance : 1 maintenance and repair instructions; 2 schedule of periodic maintenance; 3 list of replaceable parts; and 4 log for records of inspections and maintenance, listing identified non- conformities and their targeted completion dates. 4. Weekly testing and inspections 1 all public address systems and general alarm systems are functioning properly; and 2 breathing apparatus cylinders do not present leakages. 5. Monthly testing and inspections Monthly inspection should be earlier out to ensure that : 1 all fireman’s outfits, fire extinguishers, fire hydrants, hose and nozzles are in place, properly arranged, and are in proper condition; 2 all fixed fire-fighting system stop valves are in the proper open or closed position, dry pipe sprinkler systems have appropriate pressures as indicated by gauges; 3 sprinkler system pressure tanks have correct levels of water as indicated by glass gauges; 4 all sprinkler system pumps automatically operate on reduction of pressure in the systems; 5 all fire pumps are operated; and 6 all fixed fire-extinguishing installation using extinguishing gas are free from leakage. 6. Quarterly testing and inspections Quarterly inspection should be carried out to ensure that: 1 all automatic alarms for the sprinkler system are tested using the test valves for each section; 2 the international shore connection is in proper condition; 3 lockers providing storage for fire-fighting equipment contain proper inventory and equipment is in-proper condition; 4 all fire doors and fire dampers are tested for local operation; and 5 all CO2 bottle connections for cable operating system clips should be checked for tightness on fixed fire-extinguishing installations. 7. Annual testing and inspections Annual inspections should be carried out to ensure that: 1 all fire extinguishers are checked for proper location, charging pressure and condition; 2 fire detection systems are tested for proper operation, as appropriate; 3 all fire doors and dampers are tested for remote operation; 4 all foam-water and water-spray fixed fire-fighting systems are tested for operation; 5 all accessible components of fixed fire-fighting system are visually inspected for proper condition; 6 all fire pumps, including sprinkler system pumps, are flow tested for proper pressures and flows; 7 all hydrants are tested for operation; 8 all antifreeze systems are tested for proper solution; 9 sprinkler system connections from the ship’s fire main are tested for operation. 10 all fire hoses are hydrostatically tested; 11 breathing apparatus air recharging systems checked for air quality; 12 control valves of fixed fir-fighting system should be inspected; and 13 air should be blown through the piping of extinguishing gas systems. 8. Five-year service Further to engine circular No. 17 dated 08.10.2003, the following inspection and tests are also to be carried out at least once every five years. 1 hydrostatic testing for all SCBA’s cylinders; and 2 control valves of fixed fire- fighting systems should be internally inspected. |  |
| Back to ENGG circulars main page |  |