Survey

Draft Merchant Shipping (Fire Appliances) Rules 2025

Note:

- Text highlighted in yellow needs to be updated later as the text is prone to numbering changes and needs to be manually modified. They can be linked during finalization once the draft document is frozen.

- Text coloured red is amended from the previous notified rule as mentioned in the recital.

Contents

PART I - PRELIMINARY	5

1.  Short title, commencement and application:	5

2.  Definitions:-	6

3.  Classification of ships	9

A-Passenger ships	9

B—Ships other than passenger ships	9

PART II – FIRE PREVENTION AND FIRE APPLIANCES:	10

Section A—PASSENGER SHIPS	10

4.  Application:-	10

5.  Fire petrols, detections, alarm and public address systems :-	10

6.  Fire pumps, fire main, water service pipes, hydrants, hoses and nozzles.	11

6(A) Fire Doors	13

7.  Portable fire extinguishers in accommodation, cargo and service spaces :--	13

8.  Fixed fire extinguishing systems in cargo spaces.	14

9.  Machinery Spaces, General :	14

10.      Machinery Spaces of Category-A:	15

11. SPACES CONTAINING STEAM TURBINE OR ENCLOSED STEAM ENGINES :	16

12. FIRE EXTINGUISHING APPLIANCES IN OTHER MACHINERY SPACES :	17

13. SPECIAL REQUIREMENTS FOR MACHINERY SPACES:	17

14. INTERNATIONAL SHORE CONNECTIONS:	18

15. FIRE-MAN'S OUTFIT      :	18

16. Fire pumps, fire main, water service pipes, hydrants, hoses and nozzles--	19

17. Portable fire extinguishers--	19

18. Machinery spaces of category A and spaces containing oil fuel settling tanks--	19

19. Fire pumps, fire main, water service pipes, hydrants, hoses and nozzles--	20

20. Portable fire extinguishers--	21

21. Machinery spaces of category A--	21

22. Firemen's outfit--	22

23. International shore connections--	22

24. Ships of Class VI of less than 20 metres in Length-	22

25. Ships of Class VII-	22

SECTION B—SHIPS OTHER THAN PASSENGER SHIPS AND TANKERS	23

26. Application--	23

27. Fixed fire extinguishing arrangements in cargo spaces--	23

27(A) Means of Escape and Evacuation Dimensions	23

28. Fire pumps, fire mains, water service pipes, hydrants, hoses and nozzles.	24

29. Portable fire extinguishers in accommodation, cargo and service spaces.	25

30. Machinery spaces of Category-A :	26

31. Spaces Containing Steam Turbine or enclosed Steam Engines:	27

32. Fire Extinguishing Appliances in other Machinery Spaces.	28

33. SPECIAL REQUIREMENTS	28

34. FIRE ALAM AND DETECTION SYSTEM.	29

35.FIREMEN'S OUTFITS	29

36.INTERNATIONAL SHORE CONNECTION	30

37.SHIPS OF CLASS VIII UNDER 500 TONS AND SHIPS OF CLASSES IX, X, XI, XII AND XV UNDER 500 TONS BUT NOT UNDER 150 TONS--	30

38.SHIPS OF CLASSES IX, X, XI AND XII UNDER  150 TONS	32

39.SHIPS OF CLASS XIII OF 60 METRES IN LENGTH AND ABOVE:-	33

40.SHIPS OF CLASS XIII OF 45 METRES IN LENGTH AND ABOVE BUT LESS THAN 60 METRES IN LENGTH :-	33

41.SHIPS OF CLASS XIII OF 25 METRES IN LENGTH AND ABOVE BUT LESS THAN 45 METRES:--	34

42.SHIPS OF CLASS XIII OF LESS THAN 25 METRES IN LENGTH:-	34

43.SHIPS OF CLASS XIV OF 500 TONS AND ABOVE :-	35

44.SHIPS OF CLASS XIV OF 150 TONS AND ABOVE BUT LESS THAN 500 TONS :-	35

45.SHIPS OF CLASS XIV OF UNDER 150 TONS:-	36

46.SHIPS OF CLASS XV OF UNDER 150 TONS:-	36

Section C—TANKERS	38

47. GENERAL REQUIREMENTS:-	38

48.CARGO TANK PROTECTION:-	38

49.CARGO TANK PURGING AND/OR GAS FREEING:-	40

50. CARGO PUMP ROOMS:-	41

51. FIRE MAIN ISOLATING VALVES:-	41

52. FIREMEN'S OUTFITS:-	41

53. TANKERS OF CLASS VIII OF UNDER 500 TONS :-	42

54. TANKERS OF CLASS IX OF 150 TONS OR OVER BUT UNDER 500 TONS :-	42

55. TANKERS OF CLASS IX OF UNDER 150 TONS :-	42

56. TANKERS OF CLASS X :-	42

Section D-MISCELLANEOUS	42

57. Requirements for Ships Provided with Helicopter landing with or without Fuelling Facilities--	42

58. FIRE PUMPS:--	43

59. FIRE MAIN, WATER SERVICE PIPES AND HYDRANTS.—	47

60.FIRE HOSES:-	49

61. NOZZLES :--	50

63. FIRE EXTINGUISHERS:-	50

64. FIRE BUCKETS :-	53

65. SPECIAL REQUIREMENTS FOR FIXED FIRE EXTINGUISHING SYSTEMS :--	54

66. FIXED LOW-EXPANSION FOAM FIRE EXTINGUISHING SYSTEMS IN MACHINERY SPACES FITTED IN ADDITION TO REQUIREMENTS OF THESE RULES:-	54

67. FIXED FIRE EXTINGUISHING SYSTEMS NOT REQUIRED BY THESE RULES:-	55

68. FIRE CONTROL PLAN:	55

69. MEANS FOR STOPPING MACHINERY, SHUTTING OFF OIL FUEL SUCTION PIPES AND CLOSING OF OPENINGS:	56

70. AVAILABILITY OF FIRE FIGHTING APPLIANCES:	57

71. APPROVAL OF MATERIAL :	57

72. SPACES CONTAINING PARTICULAR RISKS:	58

73. REQUIREMENTS FOR SHIPS OF SPECIAL DESIGN AND LAYOUT:-	58

74. EQUIVALENTS, EXEMPTIONS AND SAVING:-	58

75. PENALTIES :-	59

76. Procedures, Forms & Authority for Survey	59

SCHEDULE I	60

SCHEDULE –II	61

Schedule IIA	62

SCHEDULE – III	63

SCHEDULE - IV	64

SCHEDULE – V	66

SCHEDULE - VI	67

SCHEDULE – VII	70

SCHEDULE VIII	74

SCHEDULE IX	77

SCHEDULE -X	85

SCHEDULE XII	88

SCHEDULE XIII	90

SCHEDULE XIV	92

Schedule XV	99

MINISTRY OF PORTS, SHIPPING & WATERWAYS

NEW DELHI, DD, MMMM, 2026
NOTIFICATION

Merchant Shipping (Fire Appliances) Rules 2025

G.S.R. XXX—Whereas a draft of the  Merchant Shipping (Fire Appliances) Rules, 2025 was published in the Gazette of India, Part XXX, Section XXX, Sub-section XXX, dated the DD, MMMM, YYYY under the notification of the Government of India in the Ministry of Ports, Shipping & Waterways, No. G.S.R. XXX, dated the DD, MMMM, YYYY inviting objections and suggestions from all persons likely to be affected thereby till the expiry of a period of sixty days from the date of publication of the said notification in the official Gazette;

And whereas the copies of the said Gazette were made available to the public on the DD, MMMM, YYYY;

And whereas no objections or suggestions have been received;

Now, therefore, in exercise of the powers conferred by section XXX of the Merchant Shipping Act, 2025, the Central Government hereby makes the following rules, namely:

# PART I - PRELIMINARY

## 1.  Short title, commencement and application:

(1) These rules may be called the  Merchant Shipping (Fire Appliances) Rules, 2025.

(2) They shall come into force on the date of their publication in the Official Gazette.

(3)       These rules shall apply to every Indian ship and sailing vessel the keel of which is laid, or which is at a similar stage of construction on or after DD, MMMM, YYYY.

(4)       Subsequent amendments adopted to these Rules shall apply to ships whose keels are laid or which are at a similar stage of construction on or after the effective date such respective amendments, unless expressly provided otherwise.

(5) They shall not apply to any such ship or sailing vessel the keel of which was laid before the DD, MMMM, YYYY. and the provisions of the Merchant Shipping (Fire Appliances) Rules, 1990 shall apply to such ships or sailing   vessel.

Provided that the Director General of Shipping may after the commencement of these rules, require by order in writing, the owner of any such ship or sailing vessel, having regard to any structural changes made in such ships or sailing vessel, to comply with any or all of the requirements specified in these rules.

(6) The Merchant Shipping (Fire Appliances) Rules, 1990, as amended by the Merchant Shipping (Fire Appliances) Amendment Rules, 1994, are hereby repealed and superseded by these rules, except as respects things done or omitted to be done under the said rules.

## 2.  Definitions:-

In these rules, unless the context otherwise requires

(a) 'Act' means the Merchant Shipping Act, 2025.

(b) 'accommodation spaces' means public spaces corridors and lobbies, stairways, lavatories, cabins, offices, hospitals, hair dressing saloons, pantries, not containing cooking appliances, lockers, games and hobbies rooms and spaces similar to any of the fore-going and trunks to such spaces allocated to passenger or crew;

(c) 'approved’ means approved by the Chief Surveyor with the Government of India;

(d) 'bulkhead deck' is the uppermost deck upto which the transverse water-tight bulkheads are carried;

(e) 'cargo space' means spaces used for cargo including cargo oil tanks, slop tanks and trunks to all such spaces;

(f)  "chemical tanker" means a tanker constructed or adapted and used for the carriage in bulk of any liquid product of a flammable nature listed in either,--

(i)  chapter 17 of the "International Code for the Construction and Equipment of Ships Carrying Dangerous Chemicals in Bulk"; or

(ii)  chapter VI of the Code for the construction and Equipment of Ships Carrying Dangerous Chemicals in Bulk.

whichever is applicable.

(g) "closed ro/ro space" is a ro/ro cargo space which is not an open ro/ro space and not a weather deck;

(h) "combination carrier" means a tanker designed to carry oil or solid cargo in bulk;

(i)  "control station"  means spaces in which radio or main navigating equipment, or the emergency source of power or the central fire detection equipment, or fire control equipment, or fire extinguishing installations are located, or a control room located outside a propulsion machinery space;

(j)  "crew space" means crew accommodation provided for the exclusive use of the crew ;

(k) "crude oil" means any oil occurring naturally in the earth whether or not treated to render it suitable for transportation and includes :

(i)  crude oil from which certain distillate fractions may have been removed; and

(ii)       crude oil to which certain distillate fraction may have been added.

(l)  "deadweight" means the difference in tonnes between the displacement of a ship in a water of a specific gravity of 1.025 at the load line corresponding to the assigned summer freeboard and the lightweight of the ships;

(m)       "gas carrier" means a tanker constructed or adapted and used for the carriage in bulk of any liquified gas or other products of a flammable nature listed in either:

(i)  chapter 19 of the International Code for the Construction and Equipment of Ships Carrying Liquified Gases in Bulk; or

(ii)     chapter XIX of the Code for the Construction and Equipment of Ships Carrying Liquified Gases in Bulk;

whichever is applicable.

(n) "guidelines for inert gas systems" forms part of the publication "Inert Gas Systems" 1983 edition published by  the International Maritime Organisation;

(o) "length" in relation to a registered ship, means the registered length, and in relation to an unregistered ship, means the length from the fore part of the stem to the aft side of the head of the stern post or, if no stern post is fitted to take the rudder, to the fore side of the rudder stock at the point where the rudder passes out of the hull;

(p) "machinery space" means spaces containing propelling machinery, boilers, oil fuel units, steam and internal combustion engines, generators and major electrical machinery, oil filling station, refrigerating, stabilizing, ventilation and air conditioning machinery and similar spaces and trunks to such spaces:

(q) "machinery spaces of category ‘A’ " means the spaces and trunk to such spaces which contain:--

(i)  internal combustion machinery used for main propulsion; or

(ii) internal combustion machinery used for purposes other than main propulsion where such machinery has in the aggregate a total power out put of not less than 375 K.W.; or

(iii)  any oil-fired boiler or oil fire unit;

(r)  "oil-fired boiler" means any boiler wholly or partly fired by liquid fuel;

(s) "oil fuel unit" means the equipment used for the preparation of oil fuel for delivery to an oil fired boiler or equipment used for preparation for delivery of heated oil to an internal combustion engine, and includes any oil pressure pumps, filters and heaters dealing with oil at a pressure more than 1.8 bar (0.18 N/mm2)

(t)  "open ro/ro spaces" means ro/ro cargo spaces which are open at both ends, or open at one end and provided with adequate natural ventilation effective over the entire length through permanent openings in the side plating or deck head;

(u) "passenger space" means space provided for the use of passengers;

(v)  "public spaces" include halls, dining rooms, bars, smoke rooms, lounges, recreation rooms, nurseries, libraries, cinemas, sale shops and similarly permanently enclosed spaces allocated to passengers or crew;

(w) "Reid vapour pressure" means the vapour pressure of a liquid as determined by laboratory testing in standard manner in the Reid apparatus;

(x) "ro/ro cargo spaces" means spaces not normally sub-divided in any way and extending to either a substantial length or the entire length of the ship in which goods (packaged or in bulk), in or on rail or road cars, vehicles (including road or rail tankers), trailers, containers, pallets, demountable tanks or in or on similar stowage units or other receptacles can be loaded and unloaded normally in a horizontal direction.

(y) "Schedule" appended to these rules;

(z) "service spaces" indoor galleys, pantries containing cooking appliances, laundaries, drying rooms, lockers and store rooms, paint rooms, baggage rooms, mail and specie rooms, workshops (other than those forming part of the machinery spaces) and similar spaces and trunks to such spaces;

(za)       "short international voyage" is an international voyage in  the  course  of  which a ship is not more than 200 nautical miles from a port or place in which the passengers and crew could be placed in safety.  Neither the distance between the last port of call in the country in which the voyage begins and the final port of destination nor the return voyage shall exceed 600 nautical miles.  The final port of destination is the last port of call in the scheduled voyage at which the ship commences its return voyage to the country in which the voyage began;

(zb)       "special category space" means an enclosed space above or below the bulkhead deck intended for the carriage of motor vehicles with fuel in their tanks for their own propulsion, into and from which such vehicles can be driven and to which passengers have access;

(zc)       "tons" means gross tons and in the case of ships having two gross tonnages the larger of these ;

(zd)       "weather deck" means a deck completely exposed to the weather from above and from at least two sides.

## 3.  Classification of ships

For the purpose of these rules, any Indian ship and any sea going sailing vessel shall be arranged in the following classes, namely :--

### A-Passenger ships

Class I- Passenger ships engaged on international voyages other than ships of classes II, III and IV.

Class II-Passenger ships engaged on short international voyages other than ships of class IV.

Class III-Special trade passenger ships engaged on international voyages other than ships of class IV.

Class IV-    Special trade passenger ships engaged on short international voyages.

Class V-Special trade passenger ships and passenger ships other than ships of classes VI and VII engaged on voyages other than international voyages.

Class VI-    Special trade passenger ships or passenger ships engaged on voyages on the coasting trade of India during the course of which they do not go more than 20 nautical miles from the nearest land. Provided that such ships shall not cease to be ships of class VI merely by reason of the fact that they cross during their voyage the Gulf of Kutch, Cambay or Mannar.

Class VII-   Special trade passenger ships or passenger ships engaged on voyages between ports in India during the course of which they do not go more than 5 nautical miles from the nearest land.

### B—Ships other than passenger ships

Class VIII-  Cargo ships engaged on international voyages.

Class IX-    Cargo ships (other than ships of class X) engaged on voyages which are not international.

Class X-Cargo ships engaged on the coasting trade of India (other than ships of class IX) during the course of which they do not go more than 20 nautical miles from the nearest land :

Provided that such ships shall not cease to be ships of class X merely by reason of the fact that they cross during their voyage the Gulf of Kutch, Cambay or Mannar.

Class XI-    Cargo ships engaged on voyages between ports in India during the course of which they do not go more than 5 nautical miles from the nearest land.

Class XII-    Tugs and tenders which proceed to sea but are not engaged on international voyages.

Class XIII-   Fishing vessels other than those of class XIV.

Class XIV-  Sailing vessels including sailing fishing vessels.

Class XV-   Pleasure Craft.

# PART II – FIRE PREVENTION AND FIRE APPLIANCES:

# Section A—PASSENGER SHIPS

## 4.  Application:-

(i)  Rule 5 to 15 shall apply to every ship of Class I, II, III, IV and every ship of Class V of 20 meters in length and above.

(ii)  Rules 16 to 18 shall apply to every ship of Class V of 20 metres in length.

(iii) Rules 19 to 23 shall apply to every ship of Class VI of 20 metres in length and above.

(iv) Rule 24 shall apply to every ship of Class VI if less than 20 metres in length.

(v)  Rule 25 shall apply to every ship of Class VII.

Class I, II, III, IV and every ship of Class V of 20 meters in length and above.

## 5.  Fire petrols, detections, alarm and public address systems :-

Every ship shall comply with the following, namely :

(i)  An efficient fire patrol shall be maintained in ships carrying more than 36 passengers so that an outbreak of fire may be promptly detected.

(ii)  Each member of the fire patrol shall be trained to be familiar with the arrangements of the ship as well as the location and operation of any equipment he may be called upon to use.

(iii) Manually operated call points complying with the requirements specified in Schedule VII shall be fitted throughout the accommodation spaces, service spaces and special category spaces, which will give an alarm immediately to the navigating bridge or fire control station.  Such a manually operated call point shall be positioned adjacent to each exit from every special category space.

(iv) In every special category space in which the fire patrol is not maintained by a continuous fire watch during the voyage, a fixed fire detection and fire alarm system complying with the requirements specified in Schedule VII shall be provided.

(v)  In every part of the ship which is not reasonably accessible to the fire patrol and in every cargo space (other than special category spaces) containing motor vehicles having fuel in their tanks for their own propulsion, a fixed fire detection and fire alarm system complying with the requirements specified in Schedule VII or a sample extraction smoke detection system complying with the requirements specified in Schedule VIII shall be provided.  Provided that the Chief Surveyor with the Govt. of India may, if he is satisfied that compliance with the provisions of this clause would be unreasonable on account of the short duration of the voyages on which the ship, is engaged, exempt any ship from the said requirements in respect of any part of the ship which is not accessible to the fire patrol.

(vi) In any machinery space where the main propulsion and associated machinery including sources of main electrical supply are provided with automatic or remote control under continuous manned supervision from a control room, there shall be provided a fixed fire detection and fire alarm system complying with the requirements specified in Schedule VII.

(vii)       Be so manned and equipped as to ensure that any initial fire alarm is immediately received by a responsible member of the crew at all times when at sea, or in port (except when out of service).

(viii)       A special alarm, operated from the navigating bridge or fire control station, shall be fitted to summon the crew, which may be part of the ship's general alarm system but shall be capable of being sounded independently of the alarm to the passenger spaces.

(ix) A public address system or other effective means of communication shall be available throughout the accommodation space, the service space and control station.

## 6.  Fire pumps, fire main, water service pipes, hydrants, hoses and nozzles.

(1) Every ship shall be provided with fire pumps, fire mains, water service pipes, hydrants, hoses and nozzles capable of providing at least two jets of water, not emanating from the same hydrant, capable of reaching normally accessible parts of the ship while the ship is being navigated and any store room and any part of any cargo space when empty.

(2) Every ship of 4000 tons or above shall be provided with at least three independently driven fire pumps and every ship or less than 4000 tons shall be provided with at least two such pumps, and each such pump shall be capable of delivering two jets of water specified under clause (1) and in addition shall comply with the requirements specified in rule 58.

(3) In every ship of 1000 tons and above, the arrangements of sea connections, pumps and sources of power for operating them shall be such as to ensure that fire in any one compartment will not put all the fire pumps out of action:

Provided that where arrangement in a ship is such that a fire in any one compartment could put all the fire-pumps out of action, there shall be provided in a position outside the machinery spaces, an independently driven power operated emergency fire pump and its source of power and sea connection.  Such pump shall be capable of producing at least two jets of water from any two hydrants and hoses through nozzles which shall comply with the requirements specified in sub-rule (2) of rule 61 while simultaneously maintaining a pressure of at least 2.1 bar (0.21 N/mm2) at any hydrant in the ship.

(4)(a)     Every Ship shall be provided with a fire main, water service pipes, hydrants, hoses and nozzles which shall be so arranged that they comply with the requirements specified in rules 59, 60 and 61 when all watertight door and all doors in main vertical zone bulkheads are closed.

4(b)       In every ship of 1000 tons and above, the arrangement of fire pumps, fire mains and hydrants shall be such that at least one jet of water is immediately available from any one hydrant in an interior location.  Arrangements shall also be made to ensure the continuation of the output of water by the automatic starting of a fire pump.

4(c) Every passenger ship shall be subdivided into main vertical zones not exceeding 40 m in length by A-60 divisions complying with Regulation II-2/9.2. Exceptions for small ships < 125 m shall follow FSS Code interpretation MSC/Circ.1120.

(5) In every ship at least one fire hose complete with nozzle shall be provided for every hydrant fitted in compliance with this rule and shall be used only for the purpose of extinguishing fire or for testing the fire extinguishing appliances at fire drills and surveys.

(6) In every ship.

(a) in any ro/ro cargo space or any special category space, the number of hydrants with holes shall be positioned near the accesses of such spaces and be so arranged that at least two jets of water, each from a single length of hose, not emanating from the same hydrant shall reach any part of such space.

(b) Where, in any machinery space of category A, access is provided at a low level from an adjacent shaft tunnel two hydrants fitted with hoses with dual-purpose nozzles shall be provided external to, but near the entrance of that machinery space.  Where such access is not provided from a tunnel but is provided from other space or spaces there shall be provided in one of those spaces two hydrant; fitted with hoses with dual-purpose nozzles near the entrance to the machinery space of Category A.  Such provisions need not be made when the tunnel or adjacent spaces are not part of an escape route.

(7) In every ship.

(a) at least three water-fog applicators in addition to the nozzles required under this rule shall be provided in special category spaces;

(b) carrying more than 36 passengers, each machinery space of category A shall be provided with at least two suitable water fog applicators.

## 6(A) Fire Doors

All A- and B-Class bulkhead doors shall be self-closing type, tested per IMO Res. A.754(18), capable of closing within 10–40 seconds without distortion, and fitted with remote operation from bridge control stations.

## 7.  Portable fire extinguishers in accommodation, cargo and service spaces :--

(1) Every ship shall be provided:-

(a) on each deck below the bulkhead deck, a sufficient number of portable fire extinguishers so that at least two of these shall be readily available for use in every accommodation space, service space and control station, between main vertical zones and

(b) in enclosed accommodation space, service spaces and control stations above the bulkhead deck at least one such extinguisher shall be provided for use on each side of the ship in such space, such that the total number of extinguishers provided, including those specified in Clause (a) is not less than five on a ship of 1000 tons or ever; and

(c) at least one portable fire extinguisher and a fire blanket in every galley and where the superficial deck area of any galley exceeds 45 square metres, at least two fire blankets.

(d) at least one portable fire extinguisher for use in each control station;

(e) in each special category space and cargo space intended for the carriage of motor vehicles with fuel in their tanks for their own propulsion;

(i)  for every 40 metres length of deck space, at least two portable fire extinguishers, suitable for extinguishing oil fires, so arranged that at least one extinguisher is available on each side of deck space and at least one extinguisher is available at each access to the deck space; and

(ii)  one portable foam applicator unit complying with the requirement specified in Schedule V. Provided that not less than two such applicators shall be available in the ship for use in any such space.

(2) One of the portable fire extinguishers, intended for use in each space shall be available near the entrance to that space.

## 8.  Fixed fire extinguishing systems in cargo spaces.

(1) Every ship of 1000 tons and above and every ship engaged in the carriage of dangerous goods, shall be provided in every cargo space other than special category spaces and spaces where a fixed pressure Water Spraying System is fitted in accordance with clause (b) & (c) of sub-rule (2) and fixed gas fire extinguishing system complying with the requirements specified in Schedule IV.  Provided that the Director General of Shipping may exempt any ship (other than a ship engaged in the carriage of dangerous goods) from the requirements of this sub-rule, if he is satisfied that to require compliance therewith would be unreasonable on account of the short duration of the voyages on which the ship is engaged.

(2) Every ship shall  be provided:

(a) in each special category space a fixed pressure water spraying system complying with the requirements specified in Schedule XI or any other fixed fire extinguishing system, which the Chief Surveyor with the Government of India, being satisfied after full scale test in conditions simulating a flowing petrol fire in a special category space to be not less effective in controlling fires likely to occur in such a space.

(b) in each cargo space (other than special category space) intended for the carriage of motor vehicles with fuel in their tanks for their own propulsion a fixed pressure water spraying system complying with the requirements specified in Schedule XI or a fixed gas fire extinguishing system complying with the requirements specified in Schedule IX.

(c) in each open ro/ro cargo space having a deck over and each closed ro/ro cargo space not capable of being sealed, a fixed pressure water spraying system complying with the requirements specified in Schedule XI.

## 9.  Machinery Spaces, General :

Every ship shall be provided with appliances capable of injecting rapidly and simultaneously at least two jests of water not emanating from the same hydrent at least one of which shall be from a single length of hose reaching any part of banker of machinery spaces normally accessible to crew when all water-tight doors in the main vertical zone bulk heads are closed.

## 10.      Machinery Spaces of Category-A:

Every ship with machinery space of category-A.

(1) Shall be provided in such spaces:-

(a) at least two fire hydrants, one on the port side and the other on the starboard side for each such hydrants, one fire hose complete with a nozzle and one spare fire hose complete with nozzle ;

(b) at least one of the following fixed fire extinguishing installations, namely:-

(i)  a fixed pressure water spraying system complying with the requirements specified in Schedule XII,

(ii)  a fixed gas fire extinguishing system complying with the requirements specified in Schedule IX,

(iii) a fixed high expansion foam system complying with the requirements specified in Schedule X.

Explanation—For the purpose of this rule, if the engine and boiler rooms are not entirely separated from each other by a bulkhead and if fuel oil can draw from the boiler room into the engine room, the combined engine and boiler rooms shall be considered as one single machinery space.

(2) In addition to the requirements of Clause (1) there shall be provided :-

(a) in each boiled room--

(i)  not less than one foam type fire extinguisher of at least 135 litres capacity or CO2 fire extinguisher of at least 45 Killogram capacity, as may be necessary having regard to the size of the boiler room placed in such positions so as to be readily accessible in the event of fire and shall be provided with hoses on reels suitable for reaching any part of the boiler room and spaces containing any part of the oil fuel installation;

(ii)  one portable foam applicator complying with the requirements specified in Schedule V.

(b) in each firing space in each boiler room and in each space containing any part of any oil fuel installation, at least two portable fire extinguishers suitable for extinguishing oil fires;

(c) in each firing space a receptacle containing at least 0.3 cubic metre of sand, saw dust impregnated with soda or other dry material suitable for quenching oil fire in sufficient quantity together with scoops for its distribution or in the alternative additional portable fire extinguisher suitable for extinguishing oil fires.

(3) In addition to the requirements of Clause (1) there shall be provided in any space containing internal combustion type machinery:-

(i)  not less than one foam fire extinguishers of 45 litres or carbon dioxide extinguishers of at least 15 Kilograms capacity.  The extinguishers shall be sited so as to be readily accessible in the event of fire and they shall be sufficient in number to enable foam or CO2 to be directed into any part  of the fuel and lubricating oil pressure systems, gearing and other areas of high fire risk.

(ii)     not less than set of portable foam applicator unit complying with the requirements specified in Schedule V.

(iii) not less than two portable fire extinguishers suitable for extinguishing oil fires, to ensure that at least one extinguisher is not more than 10 metres distance from any position within the space.

## 11. SPACES CONTAINING STEAM TURBINE OR ENCLOSED STEAM ENGINES :

Every ship shall be provided in spaces containing steam turbine or enclosed pressure lubricated steam engines used either for main propulsion or having in the aggregate, a total power of not less than 375 KW for auxiliary purpose :-

(a) if such spaces have not been fitted with fixed fire extinguishing system specified in Clause (1)(b) of rule 10, foam fire extinguisher each of at least 45 litres capacity or carbon dioxide fire extinguishers each of at least 16 Kilograms capacity sufficient in number to enable foam or CO2  to be directed on to any part of the pressure lubrication system and on to any part of the casings enclosing pressure lubricated parts of the turbine, engines or associated gearing and any other areas of high fire risk.

(b) not less than two portable fire extinguishers suitable for extinguishing oil fires, sufficient in number, so located that no point in the space is more than 10 metres distance from an extinguisher in that space; provided that where such spaces are periodically unattended one of the fixed fire extinguishing system complying with the requirements of sub-clause (b) of clause (1) of rule 10 shall be provided in addition.

## 12. FIRE EXTINGUISHING APPLIANCES IN OTHER MACHINERY SPACES :

In every ship where a fire hazard exists in any machinery space for which no specific provisions for fire extinguishing appliances are specified in rule 10 or 11, there shall be provided in or adjacent to that space sufficient number of portable fire extinguishers to ensure that at least one extinguisher is not more than 10 metres distance from any position within that space unless equivalent means of fire extinction are provided.

## 13. SPECIAL REQUIREMENTS FOR MACHINERY SPACES:

In every ship :-

(1) in any machinery space of category-A, to which access is provided at a low level from an adjacent shaft tunnel there shall be provided in the shaft tunnel, on the side remote from that machinery space, a light steel screen-door which shall be capable of being operated from each side in addition to any water-tight door,

(2) there shall be provided:-

(a) in each special category space a power ventilation system sufficient to give at least 10 air changes per hour;

(b) in each cargo space other than special category spaces, intended for the carriage of motor vehicles with fuel in their tanks for their own propulsion, power ventilation system sufficient to give at least 10 air changes per hour for ship carrying more than 36 passengers and 6 air changes per hour for ships carrying less than 36 passengers ;

(3) the power ventilation system referred to in sub-rule (2) shall be entirely separate from other ventilation systems and shall be operated at all times when vehicles are in such spaces. Ventilation ducts serving such spaces capable of being effectively sealed shall be separated for each such space.  The system shall be capable of being controlled from a position outside such spaces.  In addition :--

(a) the ventilation system shall be such as to prevent air stratification and the formation of air pockets;

(b) an indicator to indicate on the navigating bridge any loss or reduction of the required ventilating capacity shall be provided;

(c) arrangements shall be provided to permit a rapid shut-down and effective closure of the ventilation system in case of fire, taking into account the weather and sea conditions

(d) Ventilation ducts traversing different fire zones shall be fitted with automatic fire dampers of A-60 equivalent material, actuated through the fire-detection system.

(e) Control stations shall maintain positive pressure ≥ 50 Pa above adjacent spaces.

## 14. INTERNATIONAL SHORE CONNECTIONS:

Every ship shall be provided with at least one international shore connection complying with the requirements specified in Schedule I, to enable water to be supplied from another ship or from the shore, to the fire main and necessary facilities for enabling such a connection to be used on both sides of a ship.

## 15. FIRE-MAN'S OUTFIT      :

(1) Every ship shall be provided with at least:--

(a) Two fireman's outfit; and

(b) two fireman's outfits and two sets of personal equipment for every 80 metres (or part thereof) of the aggregate of the length of all passenger spaces and service spaces on the deck which carries such spaces, or if there is more than one such deck, on the deck which has one largest aggregate or such lengths :

(2) for fireman's outfit which includes a self contained breathing apparatus, one spare charge for each such apparatus.  Every fireman's Outfit and personal equipment referred to in sub-rule (1) shall comply with the requirements specified in Schedule-VI.

(3) At least two of the fireman's outfit referred to in sub-rule (1) shall include breathing apparatus of air hose type and the remaining shall include breathing apparatus of the self contained type. Provided that where the air hose of an air hose type breathing apparatus has, in order to comply with para (3) of Schedule VI, to exceed 36 metres in length, an additional breathing apparatus of self-contained type shall be provided on board the ship.

(4) Every ship carrying more than 36 passengers shall be provided for each pair of breathing apparatus one water for applicator which shall be stored adjacent to such apparatus.

(5) The fireman's outfits on sets of personal equipment referred to in sub-rule (1) shall be so stored as to be easily accessible and ready for use and where more than one fireman's outfits or more than one set of personal equipment is carried they shall be stored in widely separated positions.  At least two fireman's outfits and one set of personal equipment shall be available at any one storage position.

(6) Every accommodation corridor and machinery space shall carry Emergency Escape Breathing Devices (EEBDs) of 10-min duration approved to Res. MSC.98(73). Each fireman’s outfit SCBA shall have 1,200 L air capacity, 30-min operation, and 200 L reserve alarm.

SHIPS OF CLASS V OF LESS THAN 20 METRES IN LENGTH

## 16. Fire pumps, fire main, water service pipes, hydrants, hoses and nozzles--

Every ship of class V of less than 20 metres in length shall be provided in a place outside the machinery spaces a power or hand operated pump with a permanent sea connection and a hose with a 10 millimetre diameter nozzle capable of producing a jet of water having a throw of not les than 6 metres, capable of being directed to any part of the ship.

## 17. Portable fire extinguishers--

Every ship of class V of less than 20 metres in length shall be provided with at least one portable fire extinguisher in each of the passenger spaces above the bulkhead deck, and with at least two portable extinguishers in each of the crew spaces and in each of the passenger spaces below the deck.  At least one portable fire extinguisher shall be available for use in any galley.

## 18. Machinery spaces of category A and spaces containing oil fuel settling tanks--

(1) Every ship of class V of less than 20 metres in length shall be provided--

(a) in any space containing any oil-fired boiler, on fuel setting tank or oil fuel unit, not less than one foam fire extinguisher of at least 45 litres capacity or carbon dioxide extinguishers of at least 16 kilogrammes capacity, which shall be placed so as to be readily accessible in the event of a fire shall be sufficient in number of enable foam or carbon dioxide to be directed on to any part of the boiler room or space containing any part of the oil fuel installation;

(b) in such firing space and in each space which contains any part of any oil fuel installation at least two portable fire extinguishers suitable for extinguishing oil fires; and

(c) in each firing space a receptacle containing at least 0.3 cubic metre of sand or other dry material suitable for extinguishing oil fires together with a scoop for its distribution, or an additional portable fire extinguisher suitable for extinguishing oil fires.

(2) Every such ship of 15 metres in length and above but less than 20 metres in length, shall be provided in each space containing internal combustion type propulsion machinery, at least five portable fire extinguishers suitable for extinguishing oil fires, and every such ship of less than 15 metres in length shall be provided with at least three such portable fire extinguishers in such spaces :

Provided that where the internal combustion machinery is situated in a space to which sub-rule (1) applies, only two such portable fire extinguishers need be provided in addition to the extinguishers required by that sub-rule.

SHIPS OF CLASS VI OF 20 METRES IN LENGTH AND ABOVE

## 19. Fire pumps, fire main, water service pipes, hydrants, hoses and nozzles--

(1) Every ship of class VI of 20 metres in length and above shall be provided with fire pumps, fire main, water service pipes, hydrants, hoses and nozzles whereby at least one jet of water can reach any part of the ship normally accessible to the passengers or crew while the ship is being navigated and any store room and any part of any cargo space when empty.

(2) Every such ship shall be provided with at least one fire pump operated by power, which shall be capable of delivering at least one jet of water from any fire hydrant, hose and nozzle provided in the ship and shall comply with the requirements of rule 58.

(3) Every such ship fitted with oil-fired boilers or internal combustion type propulsion machinery shall be provided with an additional fire pump which shall be permanently connected to the fire main but which may not be required to be operated by power.  Such pump and its source of power, if any, shall not be situated in the same compartment as the pump required under sub-rule (2) and shall be provided with a permanent sea connection situated outside the machinery space.  If such a pump is operated by power, it shall comply with the requirements of sub-rule (2) and if it is manually operated it shall be capable of producing a jet of water having a throw of not less than 6 metres from nozzles.

(4) Every such ship shall be provided with a fire main, water service pipes, hydrants, hoses and nozzles which shall comply with the requirements specified in rules 59, 60 and 61.

(5) Every such ship shall be provided with at least one fire hose for every hydrant

(6) Every such ship fitted with oil-fired boilers or internal combustion type machinery shall be provided with at least one fire hydrant in each space containing such boilers or machinery; with a nozzle for every fire hose at every hydrant fitted in such spaces.

## 20. Portable fire extinguishers--

Every ship of class VI of 20 metres in length and above shall be provided with at least one portable fire extinguisher in each of the passenger spaces above the bulkhead deck, and with at least two such extinguishers in each of the crew spaces and the passenger space below that deck.  At least one portable fire extinguisher shall be available for use in any gallery.

## 21. Machinery spaces of category A--

(1) In every ship of class VI of 20 metre, in length and above shall be provided, for the protection of any machinery space of category A, at least one of the fixed fire extinguishing installations required under Clause (1) (b) of rule 10.

(2) In addition to the requirements specified in sub-rule (1), there shall also be provided-

(a) in each boiler room not less than two foam fire extinguishers of at least 45 litres capacity or carbon dioxide fire extinguishers of at least 16 kilogrammes capacity and shall be placed so as to be readily accessible in the event of fire and they shall be sufficient in number to enable foam or carbon dioxide to be directed on to any part of the boiler room or spaces containing any part of the oil fuel installations;

(b) in each firing space and in each space which contains any part of any oil fuel installation at least two portable fire extinguishers suitable for extinguishing oil fires;

(c) in each firing space a receptacle containing at least 0.3 cubic metre of sand or other dry material suitable for extinguishing oil fires together with a scoop for its distribution, or an additional portable fire extinguisher suitable for extinguishing oil fires.

(3) In addition to the requirements of sub-rule (1) there shall be provided in any machinery space containing internal combustion type machinery:

(a) one foam fire extinguisher of at least 45 litres capacity or a carbon dioxide fire extinguisher of at least 16 kilogrammes capacity; and

(b) not less than two portable fire extinguishers suitable for extinguishing oil fires, so located that an extinguisher is not more than 10 metres distance from any point in such machinery space.

## 22. Firemen's outfit--

every ship of class VI of 20 metres in length and above shall carry one fireman's outfit for each 30 metres (or part thereof) of the registered length of the ship, complying with the requirements specified in Schedule VI.

## 23. International shore connections--

every ship of class VI of 500 tonnes and above shall be provided with at least one international shore connection complying with the requirements specified in the Schedule I, to enable water to be supplied from another ship or from the shore to the fire man and necessary facilities for enabling such a  connection to be used on both sides of a ship.

## 24. Ships of Class VI of less than 20 metres in Length-

Provisions of Rules 16 to 18 (both inclusive) shall apply to ships of Class VI of less than 20 metres in length.

## 25. Ships of Class VII-

(1) Provisions of rules 19 to 23 (both inclusive) shall apply to ships of Class VII of 20 metres in length and above

(2) Provisions of rules 16 to 18 (both inclusive) shall apply to ships of Class VII of less than 20 metres in length.

# SECTION B—SHIPS OTHER THAN PASSENGER SHIPS AND TANKERS

## 26. Application--

Save as otherwise provided, the provisions of rules 27 to 36 (both inclusive) shall apply to ships of Classes VIII, IX, X, XI, XII and XV of 500 tons and above.

## 27. Fixed fire extinguishing arrangements in cargo spaces--

(1) Every such ship engaged in the carriage of dangerous goods shall be provided.--

(a) a fixed gas fire extinguishing system complying with the requirements specified in Schedule IX for every cargo space (other than ro/ro cargo space not capable of being sealed); and

(b) a fixed pressure water spraying system complying with the requirements specified in Schedule XI for every ro/ro cargo space not capable of being sealed.

(2) Every such ship there shall be provided.--

(a) for every ro/ro cargo space capable of being sealed and for every cargo space (other than a ro/ro space) intended for the carriage of motor vehicles with fuel in their tanks for their own propulsion a fixed pressure water spraying system complying with the requirements specified in Schedule XI or a fixed gas fire extinguishing system complying with the requirements

(b) for every ro/ro cargo space not capable of being sealed a fixed pressure water spraying system complying with the requirements specified in Schedule XI.

(3) Every such ship of 2000 tons and above other than ships to which sub-rule (1) applier shall be provided a fixed gas fire extinguishing system complying with the requirements specified in Schedule IX for every cargo space.  Provided that the Chief Surveyor with the Government of India may exempt any ship from the requirements of this sub-rule if--

(i)  the ship is constructed and solely intended for the carriage of ore, coal, grain, unseasoned timber or any other non-combustible cargoes or cargoes which, in his opinion constitute a low fire risk; and

(ii)  the ship is fitted with steel hatch covers and effective means of closing all ventilators and other openings leading to the cargo spaces.

## 27(A) Means of Escape and Evacuation Dimensions

(a) Clear stairway width =W = 900 mm minimum + 10 mm for each person beyond 90 persons served.

(b) Evacuation timing shall be demonstrated to meet safe egress within 10 minutes (passenger ships) or 5 minutes (cargo ships).

(c) Arrangements to comply with FSS Code Ch. 13.2–13.4.

(d) Escape trunks, stair wells and control stations shall be provided with a pressurization system maintaining a minimum of 50 Pa to prevent smoke ingress when any door is opened, as per FSS Ch. 15.3.

## 28. Fire pumps, fire mains, water service pipes, hydrants, hoses and nozzles.

(1) Every such ship shall  be provided with fire pumps, fire-mains, water service pipes, hydrant, house and nozzles which shall be capable of delivering at least two jets of water so as to reach any part of the ship normally accessible to the passengers and crew while the ship is being navigated, and any store room and any part of any cargo space when empty.

(2) (a) Every such ship, which is less than 1000 tons shall be provided with at least one fire pump operated by power, having a capacity of not less than 25 cubic metres per hour, which shall be capable of delivering at least one jet of water simultaneously from each of any two fire hydrants, hoses and nozzles provided in the ship and shall comply with the requirements of rule 58.

(b) In every such ship, in addition to the fire pumps required under this rule, one of the other pump shall be fitted in the machinery space such as the general service, bilge and ballast pump, which shall be capable of providing water to the fire main at the capacity and pressure of the fire pumps.

(c) Every such ship of 1000 tons and above shall be provided with at least two fire pumps operated by power.  Each pump shall be capable of delivering at least one jet of water simultaneously from each of any two fire hydrants, hoses and nozzles provided in the ship and shall comply with the requirements of rule 58.

(3) (a) If in any such ship fire in any one compartment could put all the fire pumps out of action, an independently driven power operated emergency fire pump and its source of power and sea connection shall be provided in a position outside the machinery spaces.

(b) In every such ship which is under 1000 tons, such emergency fire pump shall be capable of delivering at least one jet of water simultaneously from each of any two hydrants and hoses through nozzles which shall comply with rule 61(1) while maintaining a pressure of at least 2.1 bar at any hydrant in the ship and for such ships of 1000 tons or over, the pressure at any hydrant shall not be less than 2.5 bar.

(c) In every such ship of 2000 tons or over such emergency fire pump shall meet the requirements specified in rule 58(3).

4 (a) Every such ship shall be provided with a fire main, water service pipes, hydrants, hoses and nozzles which shall comply with rules 59, 60 and 61.

(b) In every such ship the number of fire hoses shall be in addition to those required for any machinery spaces, one fire hose for each 30 metres f(or part thereof), length of the ship but in no case less than 5 hoses in a ship of 1000 tons and over and not less than 3 in a ship under 1000 tons.  Such hoses shall have a total length of at least 60 per cent of the length of the ship.  In addition there shall be provided one spare fire hoses, complete with couplings and nozzles:

Provided that the Chief Surveyor with the Government of India may require a greater number of hoses to be carried so as to ensure that hoses in sufficient number are available and accessible at all time, having regard to the size and type of ship and nature of services.

(5) All hydrants in machinery spaces of such ships fitted with main or auxiliary oil fire boilers of internal combustion type of machinery shall be provided with hoses complete with nozzles.  In each such space at least two fire hydrants one on port and one on the starboard side; and in addition where there is access to the machinery space of any such ship by way of a shaft tunnel, a fire hydrant should be provided in the tunnel at the end adjacent to that space.

(6) In every such ship there shall be provided in ro/ro cargo spaces at least three water for applications in addition to the nozzles required by this rule.

(7) In every such ship in every ro/ro cargo space the  number of hydrants with hoses shall be so arranged that at least two jets of water each from a single length of hose not emanating from the same hydrant length of hose not emanating from the same hydrant may reach any part of such space and such hydrants shall be positioned near the accesses to such space.

## 29. Portable fire extinguishers in accommodation, cargo and service spaces.

Every such ship shall be provided with--

(a) portable fire extinguishers not being less than fire in a ship of 1000 tons or above and not less than three in a ship of 500 tons and above but less than 1000 tons to ensure that at least one such extinguisher is readily available for use in any part of the accommodation spaces, service spaces and control stations.

(b) in each ro/ro cargo space intended for the carriage of motor vehicles with fuel in their tanks for their own propulsion--

(i)  at least two portable fire extinguishers suitable for extinguishing oil fires for every 40 metres length of deck space so arranged that at least one extinguisher is available on each side of such space and at least one extinguisher is available at each access to such space.

(ii)     one foam applicator complying with the requirements specified in Schedule V :

Provided that not less than two such applicators shall be available in the ship for use in any such space.

## 30. Machinery spaces of Category-A :

Every such ship with machinery space of category-A, shall be provided--

(1) in such machinery spaces--

(a) at least two fire hydrants one on both sides of the ship for each such hydrants, one fire hose complete with nozzle and one space fire hose complete with nozzle.

(b) at least one of the following fixed fire extinguishing installations namely :-

(i)  a fixed pressure water spraying system complying with the requirements specified in Schedule XII.

(ii)  a fixed gas fire extinguishing system complying with the requirements of Schedule IX.

(iii) a fixed high expansion foam system complying with the requirement specified in Schedule X.

EXPLANATION: - For the purpose of this rule, if the engine and boiler rooms are not entirely separated from each other by a bulk head and if fuel oil can drain from the boiler room into the engine room, the combined engine and boiler rooms shall be considered as one single machinery space.

(2) In each boiler room--

(i)  not less than one foam type fire extinguisher of at least 135 litres capacity or Co2 fire extinguisher of at least 45 Kilogramme capacity as may be necessary having regard to the size of the boiler room, placed in such position so as to be readily accessible in event of fire, with hoses on reels suitable for reaching any part of the boiler room and spaces containing any part of the oil fuel installation;

(ii)  one portable foam applicator complying with the requirements specified in Schedule V:

(iii) in each, firing space and in each space containing any part of any oil fuel installation at least two portable fire extinguishers suitable for extinguishing oil fires;

(iv) in each firing space, a receptacle containing at least 0.3 cubic metre of sand, saw dust impregnated with soda or other dry material suitable for quenching oil fire insufficient quantity together with scoops for its distribution or an additional portable fire extinguisher suitable for extinguishing oil fires.

(3) in any space containing internal combustion type machinery :-

(i)  not less than one foam fire extinguishers of 45 litres or carbon dioxide extinguishers or at least 16 Kilogramme capacity sufficient in number to enable foam or Co2 to be directed into any part of the fuel and lubricating oil pressure systems, gearing and other areas of high fire risk.;

(ii)  not less than one set of portable foam applicator unit complying with the requirements specified in Schedule V;

(iii) not less than two portable fire extinguishers suitable for extinguishing oil fires to ensure that at least one extinguisher is not more than 10 metres distance from any position within the space.

## 31. Spaces Containing Steam Turbine or enclosed Steam Engines:

Every such ship shall be provided in spaces containing steam turbine or enclosed pressure lubricated steam engines used either for main propulsion or having in the aggregate a total power of one less than 375 Kw for auxiliary purposes:-

(a) if such spaces have not been fitted with fixed fire extinguishing system specified in clause (1)(b) of rule 30, foam fire extinguish each of at least 45 litres capacity or carbon dioxide fire extinguishers each of at least 16 Kilogramme capacity sufficient in number to enable foam or Co2 to be directed on to any part of the pressure lubrication system and on to any part of the castings enclosing pressure lubricated parts of the turbine, engines or associated gearing and any other areas of high fire risk:

(b) not less than two portable fire extinguishers suitable for extinguishing oil fires, sufficient in number, so located that no point in the space is more than 10 metres distance from an extinguisher in that space.

## 32. Fire Extinguishing Appliances in other Machinery Spaces.

Every ship where a fire hazard exists in any machinery space for which no specific provisions for fire extinguishing appliances are specified in rule 30 and 31, shall be provided in or adjacent to such space a sufficient number of portable fire extinguishers to ensure that at least one extinguisher is not more than 10 metres distance from any position within such space or other equivalent means of fire extinction.

## 33. SPECIAL REQUIREMENTS

In every ship--

(1) in any machinery space of category 'A' to which access is provided at a low level from an adjacent shaft tunnel there shall be provided in addition to any water-tight door and on the side remote from that machinery space, a light steel fire screen door, which shall be capable of being operated from each side;

(2) there shall be provided in each closed ro/ro cargo space and each cargo space intended for the carriage of motor vehicles with fuel in their tanks for their own propulsion, power ventilation system to provide at least six air changes per hour based on an empty hold.  Ventilation fans shall be run continuously whenever vehicles are on board.  The system shall be entirely separate from other ventilating systems.  Ventilation ducts serving such spaces capable of being effectively sealed shall be separated for each cargo space.  The system shall be capable of being controlled from a position outside such spaces.  In addition :--

(a) the ventilation system shall be such as to prevent air stratification and the formation of air pockets;

(b) an indicator to indicate any loss of the required ventilating capacity on the navigating bridge:

(c) arrangements shall be provided to permit a rapid shutdown and effective closure of the ventilating system in case of fire taking into account the weather and sea conditions.

## 34. FIRE ALAM AND DETECTION SYSTEM.

(1) Every ship shall be provided with a fixed fire detection and fire alarm system complying with the requirements specified in Schedule VII in any machinery space where :

(a) the installation of automatic and remote control systems and equipment has been approved in lieu of continuous manning of such space ; or

(b) the main propulsion and associated machinery including sources of main electrical supply are provided with some automatic or remote control and are under continuous manned supervision from a control room.

(2) In every such ship there shall be provided in each ro/ro cargo space a fixed fire detection and fire alarm system complying with the requirements specified in Schedule VII.

(3) In every such ship shall be provided in each cargo space (other than ro/ro cargo spaces) intended for the carriage of motor vehicles with fuel in their tanks for their own propulsion either a fixed fire detection and fire alarm system complying with the requirements specified in Schedule VII  or a sample extraction smoke detection system complying with the requirements specified in Schedule VII .

## 35.FIREMEN'S OUTFITS

(1) Every ship shall carry firemen's outfits which shall comply with requirements specified in Schedule VI in accordance with the following scale:-

| Tonnage of the ship | Number of outfits |
| --- | --- |
| 500 tons and over but under 2500 tons | 2 |
| 2500 tons and over but under 4000 tons | 3 |
| 4000 tons and over | 4 |

(2) At least one such outfit carried in any such ship shall include a breathing apparatus of air hose type and the remainder shall include breathing apparatus of self-contained type.

Provided that where the air hose of an air hose type breathing apparatus has, in order to comply with para (3) of Schedule VI to exceed 36 metres in length, one breathing apparatus of the self-contained type shall be provided on board the ship.

(3) The firemen's outfits or sets of personal equipment shall be so stored as to be easily accessible and ready for use and where more than one such set is carried, they shall be stored in widely separated position.

## 36.INTERNATIONAL SHORE CONNECTION

Every ship shall be provided with--

(1) at least one international shore connection complying with the requirements of Schedule I to enable water to be supplied from another ship or from the shore to the fire main.

(2) fixed provisions shall be made to enable such a connection to be used on both sides of the ship.

## 37.SHIPS OF CLASS VIII UNDER 500 TONS AND SHIPS OF CLASSES IX, X, XI, XII AND XV UNDER 500 TONS BUT NOT UNDER 150 TONS--

(1) The provisions of this rule shall apply to ships of Class VIII under 500 tons and ships of Classes IX, X, XI, XII and XV under 500 tons but not under 150 tons.

(2) Every ship shall be provided with---

(a) Fire pumps, fire mains, water service pipes, hydrants hoses and nozzles whereby at least one jet of water can reach any part of the ship normally accessible to the passengers or crew while the ship is being navigated and any store room and any part of any cargo space when empty:

(b) at least one fire pump operated by power complying with the requirements of rule 58, which shall be capable of delivering at least one jet of water from any fire hydrant hose and nozzle provided in the ship;

(c) if fitted with oil-fired boiler or internal combustion type propelling machinery, an additional fire pump and its source of power and sea connection in a position outside the spaces containing such boilers or machinery and if such pump is operated by power, it shall comply with the requirements of the preceding clause and if it is manually operated, it shall be provided with a hose and 10 millimetres diameter nozzle capable of producing a jet of water having a throw of not less than 6 metres capable of being directed on to any part of the ship;

(d) a fire main, water service pipes and hydrants complying with the requirements of rule 59 and at least three fire hoses and nozzles complying with rules 60 & 61;

(e) at least three portable fire extinguishers so situated as to be readily available for use in the accommodation and service spaces;

(f)  at least one of the fixed fire extinguishing installations specified in Clause (1)(b) of rule 30 for the protection of any space containing any oil-fired boiler, oil Fuel Setting Tank or Oil Fuel Unit;

(g) at least two portable fire extinguishers suitable for extinguishing oil fires; in each boiler room and in each space which contains any part of any oil fuel installation;

(h) a receptacle containing at least 0.3 cubic metre of sand or other dry material suitable for extinguishing oil fires together with a scoop for its distribution or an additional portable fire extinguisher suitable for extinguishing oil fires in each firing space;

(i)  if it is fitted with internal combustion propelling machinery in machinery spaces with--

(i)  portable fire extinguishers capable of discharging from or other substances suitable for quenching oil fires, as specified in the Table below :-

| Power of main engine in KW | No.of portable extinguishers |
| --- | --- |
| Upto and including 150 | 2 |
| Above 150 but not above 300 | 4 |
| Above 300 but not above 450 | 6 |
| Above 450 | 7 |

or

(ii)  two portable fire extinguishers suitable for extinguishing oil fires together with--

(a) one foam fire extinguisher of at least 45 litres; or

(b) one carbon  dioxide fire extinguisher of at least 16 kilogramme capacity.

(j)  at least one fireman's outfit which shall comply with the requirements specified in Schedule VI and which shall contain a breathing apparatus of the air hose type.

## 38.SHIPS OF CLASSES IX, X, XI AND XII UNDER  150 TONS

(1)(a)     in respect of every ship of Classes IX, X, XI and XII under 150 tons, which is 20 metres in length and above the provision of sub-rule (2) of rule 37 shall apply, subject to the conditions that fire pumps required to be provided under clause (b) of that sub-rule may be driven by the main engine.

(b) Every such ship being less than 20 metres in length shall be provided, in a position outside the machinery spaces, with a power or a hand operated pump with a permanent sea connection, hose with a 10 millimetre diameter nozzle capable of producing a jet of water having a throw of not less than 6 metres capable of being directed to any part of the Ship, and a spray nozzle suitable for use with the hose :

Provided that if such ship is of less than 9 metres in length or is an open ship of less than 20 metres is length and if such ship complies with the requirements of sub-rule (2), so far as it relates to fire buckets the requirement specified in this clause shall not be required to be complied with and if such ship does not comply with the requirement of sub-rule (3) so far as it relates to fire buckets,  shall be required to have two fire buckets one of which shall be fitted with a lanyard.

(2) Every such ship shall be provided with portable fire extinguishers or with fire buckets in accordance with the following Table:-

| Length of ship | Minimum number of extinguishers or buckets |
| --- | --- |
| Under 20 m | 2 |
| 20 m or over | 3 |

When fire buckets are provided, these shall be fitted with a lanyard.

(3) Every such ship if fitted with oil-fired boilers or internal combustion type propulsion machinery shall in addition be provided with portable fire extinguishers suitable for extinguishing oil fires in accordance with the following table :--

| Length of ship | Minimum number of extinguishers or buckets |
| --- | --- |
| Under 6 m | 1 |
| 6 m or over | 2 |

(4) Every such ship of 9 metres in length or over which is fitted with oil-fired boilers or internal combustion type propulsion machinery shall, if it is mainly or wholly constructed of wood or glass reinforced plastic and is decked in way of the machinery space, be provided with means outside the machinery space for rapidly injecting into the machinery space a quantity of fire smothering gas equivalent to at least 60 per cent of the gross volume of that space, or where the machinery space is bounded by steel bulk-heads equivalent to at least 40 per cent of the gross volume of the space.

Provided that where such ship is of less than 20 metres in length, it will be sufficient if a water spraying system supplied from a hand pump and a permanent sea connection situated outside the machinery space which may be the hand pump and the sea connection referred to in sub-rule (1)(b) is provided.  Such pump shall be connected by fixed piping to a sufficient number of water spraying nazzles suitably placed in the machinery space and capable of extinguishing oil fires.

(5) Every such ship being a fully decked ship of 20 metres in length or over shall be provided with a fireman's axe.

## 39.SHIPS OF CLASS XIII OF 60 METRES IN LENGTH AND ABOVE:-

(1) The Provisions of rules 28 to 30 (except sub-rule 2(ii) and 3(ii) of rule 30), 35 and 36 shall apply to ships of class XIII of 60 metres in length and above as they apply to ships of class XIII of 1000 tons and above, and

(2) In every such ship, a water spray system independent of any system fitted in the machinery space capable of being connected with the fire main and operable from outside the store shall be fitted in the net store.

## 40.SHIPS OF CLASS XIII OF 45 METRES IN LENGTH AND ABOVE BUT LESS THAN 60 METRES IN LENGTH :-

(1) The provisions of rules 28 to 30 (except sub-rules 2(ii) and 3(ii) of rule 30), 35 and 36 shall apply to ships of class XIII of 45 metres in length and above but less than 60 metres in length as they apply to ships of class VIII of 500 tons and above, and

(2) In every such ship, a water spray system independent of any system fitted in the machinery space capable of being connected with a fire man and operable from outside the store shall be fitted in the net store.

## 41.SHIPS OF CLASS XIII OF 25 METRES IN LENGTH AND ABOVE BUT LESS THAN 45 METRES:--

(1) The provisions of rule 37(2) (a) (b) (c) (d) (e) (i) (j) shall apply to ships of class XIII of 25 metres in length and above but les than 45 metres in length as they apply to ships of class VIII of less than 500 tons.

(2) In every such ship, the hull of which is constructed of wood or glass reinforced plastic, there shall be provided for the protection of machinery spaces a fixed fire smothering gas installation complying with the requirements specified in Schedule IX except that the quantity of free fire smothering gas provided shall be equivalent to at least 60 per cent of the gross volume of the machinery space or in the case of any such ship where the machinery space is bounded by steel bulkheads, the quantity off free fire smothering gas shall be equivalent to at least 40 per cent of the gross volume of that space.

(3) In every such ship which is not required to comply with sub-rule (2) shall be provided with at least one of the fixed fire extinguishing installations required under rule 30(1)(b) for the protection of any space containing any oil fire boiler, oil fuel settling tank or oil fuel unit in ships.

(4) In every such ship, in addition to the requirements of sub-rule (3), there shall be provided:--

(a) in each boiler room and in each space which contains any part of any oil fuel installation, at least two portable fire extinguishers suitable for extinguishing oil fires;

(b) in each firing space a receptacle containing at least 0.15 cubic metres of sand or other dry material suitable for quenching oil fires together with a scoop for its distribution, or an additional portable fire extinguisher suitable for extinguishing oil fires.

(5) In every such ship, water spray system independent of any system fitted in the machinery space and which may be connected to the fire main shall be fitted in the net store and be operable from outside the space.

## 42.SHIPS OF CLASS XIII OF LESS THAN 25 METRES IN LENGTH:-

The provisions of rule 38 shall apply to ships of class XIII of less than 25 metres in length.

## 43.SHIPS OF CLASS XIV OF 500 TONS AND ABOVE :-

The  provisions of rule 37 shall apply to all ships of Class XIV of 500 tons and above.

## 44.SHIPS OF CLASS XIV OF 150 TONS AND ABOVE BUT LESS THAN 500 TONS :-

(1)(a)     Every ship of class XIV of 150 tons and over but less than 500 tons shall be provided with at least one fire pump and fire hose with nozzle whereby a jet of water can be directed into any part of the ship.

(b)    Where the pump provided in accordance with clause (a) is situated inside spaces containing oil fired boilers or internal combustion machinery, there shall be provided outside such space a portable diesel driven pump or a hand pump with a hose and nozzle capable of delivering a jet of water having a throw of not less than 6 metres.

(c)     Every such ship shall be provided with at least 3 portable fire extinguishers for the protection of accommodation and service spaces.

(d)      Every such ship shall be provided with three fire buckets.

(2) Every such ship fitted with main or auxiliary oil fired boilers or internal combustion propelling machinery shall be provided with--

(a) a nozzle suitable for spraying water on oil;

(b) a receptacle containing 0.3 cubic metre of sand or other dry material suitable for quenching oil fires together with a scoop for distributing the contents of the receptacle.

(3) In each boiler room or space containing any part of any oil fuel installation of such ship there shall be provided at least 2 portable fire extinguishers suitable for extinguishing oil fires.

(4) In each machinery space in such ship one foam extinguisher of at least 45 litre capacity or an equivalent carbon dioxide extinguisher shall be provided.

(5) At least 2 portable extinguishers capable of discharging foam or any other substance suitable for quenching oil fires shall be provided in such ship.

## 45.SHIPS OF CLASS XIV OF UNDER 150 TONS:-

(1) Every ship of class XIV of 50 tons and above but less than 150 tons shall be provided, with a fire pump operated by power and fire hose with nozzle capable of discharging at jet of water into any part of the ship and where the fire pump is driven by main engine, a outside the machinery space with its sea connection and hose and nozzle capable of directing a jet of water having a throw not less than 6 metres.  In addition, a nozzle for spraying water suitable for quenching oil fire shall be provided.

(2) Every such ship fitted with main or auxiliary oil fired boilers or internal combustion propelling machinery shall be provided with.--

(a) a receptable containing 0.3 cubic metre of sand or other dry material suitable for quenching oil fires together with a scoop for distributing the contents of the receptacle;

(b)     at least 4 portable fire extinguishers capable of discharging foam or other substances suitable for quenching oil fires.

(3) Every such ship shall be provided with fire buckets in accordance with the following Table :-

| Ship tonnage | Minimum number of Fire buckets |
| --- | --- |
| Under 50 tons | 2 (One of which shall be fitted with lanyard) |
| Over 50 tons but not over 100 tons | 3 (two of which shall be fitted with lanyard) |
| Over 100 tons | 4 (two of which shall be fitted with lanyard) |

## 46.SHIPS OF CLASS XV OF UNDER 150 TONS:-

(1) Every ship of class XV of under 150 tons of 20 metres in length or over.--

(a) shall be provided with fire pumps fire mains, water mains, hydrants, hoses and nozzles capable of producing at least one jet of water to reach any part of the ship normally accessible to the passengers or crew while the ship is being navigated, and any store room and any part of any cargo space when empty;

(b) shall be provided with at least one fire pump operated by power which may be driven by the main engine and which shall be cabable of delivering at least one jet of water from any fire hydrant hose and nozzle provided with the ship and which shall comply with the requirements of rule 58:

(c) if fitted with boilers or internal combustion type propulsion machinery, the pump required under the preceding clause and its source of power and sea connection are not situated outside spaces containing such boilers or machinery, there shall be provided in a position outside such spaces an additional fire pump and its source of power and sea connection.  If such comply with the requirements of the preceding clause and if it is manually operated, it shall be provided with a hose and a 10 millimetre diameter nozzle through which it shall be capable of producing a jet of water having a throw of not less than 6 metres capable of being directed on to any part of the ship;

(d) In every such ship there shall be provided a fire main, water service pipes and hydrants which shall comply with the requirements of rule 59 and at least two fire hoses.

(2) Every such ship of less than 20 metres in length shall be provided in a position outside the machinery spaces with either a power or a hand operated pump with a permanent sea connection, a hose with a nozzle at least 6 millimetres in diameter capable of producing a jet of water having a throw of not less than 6 metres capable of being directed on to any part of the ship, and in addition a spray nozzle suitable for use with the hose.

Provided that if such ship is of less than 15 metres in length or is an open ship of less than 20 metres in length and if such ship complies with the requirements of sub-rule (3), so far as it relates to fire buckets, the requirements specified in this sub-rule shall not be required to be complied with and if such ship does not comply with the requirements of sub-rule (3), so far as it relates to fire buckets, shall be required to have two fire buckets one of which shall be fitted with a lanyard.

(3) Every such ship shall be provided with portable fire extinguishers or with fire buckets in accordance with the following table:--

| Length of ship | Minimum number of extinguishers or buckets |
| --- | --- |
| Under 20 m | 2 |
| 20 m or over | 3 |

(when fire buckets are provided at least one shall be fitted with a lanyard).

(4) Every such ship, if fitted with oil-fired boilers or internal combustion type propelling machinery shall, in addition, be provided with two portable fire extinguishers suitable for extinguishing oil fires.

(5) Every such ship being a fully decked ship of 20 metres in length or over shall be provided with fireman's axe.

# Section C—TANKERS

TANKERS OF CLASS VII AND IX OF 500 TONS OR OVER

## 47. GENERAL REQUIREMENTS:-

Provisions of rules 28, 29(a), 30 to 33 (1) (both inclusive), 34(1) and 36 shall apply to every tanker of class VIII and IX of 500 tons or over.

## 48.CARGO TANK PROTECTION:-

(1) Every tanker of class VIII and class IX of 500 tons or over shall be provided with a fixed deck foam system complying with the requirements specified in Schedule XIII.

Provided that the requirement of this sub-rule shall not apply to a chemical tanker having a valid certificate of fitness for the carriage of dangerous chemicals in bulk, in compliance with the requirements of the IMO Code for the Construction and equipment of ships carrying dangerous chemicals in bulk, and to a gas carrier having a valid certificate of fitness for the carriage of liquefied gases in bulk in compliance with the requirements of the IMO Code for the construction and equipment of ships carrying liquefied gases in bulk.

(2) Every tanker of class VIII and class IX of 20,000 tonnes deadweight or over constructed or adapted and used to carry crude oil and petroleum products having a closed flash point not exceeding 600C, the reid vapour pressures of which is below that of atmospheric pressure and other liquids having a similar fire hazard shall be provided with an inert gas system complying with the requirements specified in Schedule XIV:

Provided that the requirement of this sub-rule shall not apply to a chemical tanker having a valid certificate of fitness for the carriage of dangerous chemicals in bulk in compliance with the requirements of the IMO Code for the construction and equipment of ships carrying dangerous chemicals in bulk, and to a gas carrier having a valid certificate of fitness for the carriage of liquefied gases in bulk in compliance with the requirements of the IMO Code for the construction and equipment of ships carrying liquefied gases in bulk.  For these ships, alternative arrangements may be provided to the satisfaction of Chief Surveyor with the Government of India.

(3) Combination carriers shall not carry solid cargoes unless,--

(a) all cargo tanks are empty of crude oil and other petroleum products having a closed flash point not exceeding 600C and other liquids having a similar fire hazard and are gas freed; or

(b) the arrangements provided in each case are in accordance with the relevant operational requirements contained in the "Guidelines for Inert Gas Systems".

(4)(a)     Every inert gas system provided in accordance with this rule shall be designed and operated so as to render and keep the atmosphere of the cargo tanks including the slop tanks non-flammable at all times, except where such tanks are to be gas free.

(b)    In the event that the inert gas system is unable to meet the operational requirement set out above and it has been assessed that it is impractical to effect a repair, then cargo discharge, deballasting and necessary tank cleaning may only be resumed when the "emergency procedures" laid down in the "Guidelines for Inert Gas Systems" are complied with.

(5) Notwithstanding the provisions of sub-rule (2), every tanker of class VIII and class IX operating with a tank cleaning procedure using crude oil washing shall be,--

(a) fitted with an inert gas system complying with the requirements specified in Schedule XIV, and

(b) provided with fixed tank washing machines.

(6) Every tanker of class VIII and class IX fitted with a fixed inert gas system shall be provided with a closed ullage system.

(7) Other fixed fire extinguishing installations may be provided in place of those required by the foregoing provisions of this rule if each installation is equivalent to the said systems in the manner set out in clauses (a) and (b),--

(a) an installation provided in place of the inert gas system shall be deemed to be equivalent to that system, if it is,--

(i)  capable of preventing dangerous accumulation of explosive mixtures in intact cargo tanks during normal service throughout the ballast voyage and necessary intank operations; and

(ii)  so designed as to minimize the risk of ignition from the general of static electricity by the system itself.

(b) an installation provided in place of the fixed deck foam system shall be deemed to be equivalent to that system, if it is,--

(i)  capable of extinguishing spill fires and precludes ignition of spilled oil, and

(ii)  capable of combating fires in ruptured tanks.

## 49.CARGO TANK PURGING AND/OR GAS FREEING:-

(1) In every tanker of class VIII and class IX of 500 tons or over, arrangements of purging or gas freeing, or both, shall be such as to minimize the hazards due to the dispersal of flammable vapours in the atmosphere and to flammable mixtures in a cargo tank.

(2) When such tanker is provided with an inert gas system, it shall first be purged in accordance with the provisions of para (13) of Schedule XIV until the concentration of hydrocarbon vapours in the cargo tanks has been reduced to less than 2 per cent by volume.  Thereafter, venting may be at the cargo tank deck level.

(3) When such ship is not provided with an inert gas system, the operation shall be such that the flammable vapour is initially discharged,--

(a) through the vent outlets as specified in regulation 59 of chapter II-2 of the Safety Convention; or

(b) with a vertical exit velocity of a at least 20 metres per second through outlets at least 2 metres above the cargo tank deck level and through devices (other than flame screens) complying with Sixth Schedule to the Merchant Shipping (Cargo Ship Construction and Survey) Rules, 1988so as to prevent the passage of flame into the cargo tanks.  When the flammable vapour concentration in the outlet has been reduced to 30 per cent of the lower flammable limit the discharge of the vapour mixture may be at the cargo tank deck level.

## 50. CARGO PUMP ROOMS:-

(1) Except as otherwise provided in sub-rule (2), in every tanker of class VIII and class IX of 500 tons or over, each cargo pump room and each pump room having a similar hazard shall be provided with at least one of the fixed fire extinguishing systems specified in clause (1) (b) of rule 30 and shall be operated from a readily accessible position outside the pump room and where the fixed fire extinguishing system is a gas system,--

(a) the alarm system referred to in Schedule VII shall be safe for use in a flammable cargo vapour or air mixture;

(b) a notice shall be exhibited at the controls of such fixed fire extinguishing system stating that due to the electrostatic ignition hazard, the system is to be used only for fire extinguishing and not for inerting purposes;

(c) in which medium used in the cargo pump room system is also used in systems serving other spaces, the quantity of medium provided or its delivery rate need not be more than the maximum required for the largest compartment.

(2) In chemical tankers having a valid certificate of fitness for the carriage of dangerous chemicals in bulk, where the fixed fire extinguishing system referred to in sub-rule (1) is a gas system, the concentration shall be as specified in the code for the construction and equipment of ships carrying dangerous chemicals in bulk.

## 51. FIRE MAIN ISOLATING VALVES:-

In every tanker of class VIII and class IX of 500 tons or over, isolation valves shall be fitted in the fire main at poop front in a protected position and on the tank deck at intervals of not more than 40 metres so as to preserve the integrity of the fire main system in case of fire or explosion.

## 52. FIREMEN'S OUTFITS:-

In every tanker of class VIII and class IX of 500 tons and over, there shall be provided not less than four firemen's outfits complying with the requirements specified in Schedule VI, which shall be so stored as to be easily accessible and ready for use and where more than one fireman's outfits are carried, they shall be stored in widely separated positions.

## 53. TANKERS OF CLASS VIII OF UNDER 500 TONS :-

(1) The provisions of rules 37, 49 and 50 shall apply to every tankers of class VIII under 500 tons.

(2) In addition to the requirements specified in sub-rule (1), every such tanker shall be provided with at least one mobile foam appliance capable of discharging foam rapidly in the cargo manifold areas by simple operation.

## 54. TANKERS OF CLASS IX OF 150 TONS OR OVER BUT UNDER 500 TONS :-

The provisions of rules 37, 49, 50 and sub-rule (2) of rule 53 shall apply to tankers of class IX of 150 tons or over but under 500 tons.

## 55. TANKERS OF CLASS IX OF UNDER 150 TONS :-

The provisions of rules 37, 49, 50 and sub-rule 53 shall apply to tankers of class IX under 150 tons.

## 56. TANKERS OF CLASS X :-

The provisions of rules 35 and 47 to 51 shall apply to tankers of class X of 500 tons or over, the provisions of rule 54 shall apply to such tankers of 150 tons or over but under 500 tons and rule 55 shall apply to such tankers under 150 tons:

Provided that tankers over 500 tons but less than 2000 tons may comply with the provisions of sub-rule (2) of rule 53 in place of sub-rule (1) of rule 48.

# Section D-MISCELLANEOUS

## 57. Requirements for Ships Provided with Helicopter landing with or without Fuelling Facilities--

On a ship of any class having a helicopter deck, there shall be provided and stored adjacent to the means of access to such deck,--

(a) dry powder extinguishers of total capacity not less than 45 kilogrammes, and

(b) a suitable foam applicator system consisting of monitors or foam making branch pipes capable of delivering foam solution at a rate of not less than 6 litres per square metre of the area contained within a circle of diameter D metres for not less than five minutes.

Explanation-For the purpose of this rule, D is the distance across the main rotor and tail rotor in the fore and aft line of a helicopter with a single main rotor and across both rotors for a tandem rotor helicopter; and

(c) carbon dioxide extinguishers of total capacity of not less than 16 kilogrammes which shall be so equipped as to enable it to be applied to the engine area of any helicopter using the deck.

(2) The arrangement of water service pipes, hydrants, hoses and nozzles shall be such that at least two jets of water can reach any part of the helicopter deck and, any part of the fuel storage tanks and associated pumps and piping, where helicopter refueling facilities are provided.

(3) In every ship provided with helicopter refueling facilities at least two portable extinguishers suitable for fighting oil fires shall be provided adjacent to the fuel storage tanks and associated pumps and piping inn addition to any portable extinguishers required under these rules.

## 58. FIRE PUMPS:--

(1)(a)     Every fire pump required to be carried under these rules shall be operated by means of power other than the ships main engines except as expressly provided otherwise in these rules.  Sanitary, ballast, bilge or general service pumps may be accepted by the Director General of Shipping as fire pumps provided they are not normally used for umping oil and in case they are occasionally used for pumping or transferring fuel oil, suitable change-over arrangements are fitted and operating instructions are conspicuously displayed at the change-over position.

(b)(i)          In every passenger ship which is required by these rules to be provided with fire pumps operated by powers, such fire pumps (other than any emergency fire pump) shall together be capable of delivering for fire fighting purposes a quantity of water under the conditions and at the pressure specified in sub-rule (2) of not less than two-thirds of the quantity required to be dealt with by the bilge pumps provided in the ship in compliance with part I of the Merchant Shipping (Construction and Survey of Passenger Ships) Rules, 1981.

(ii)         In every ship, other than a passenger ship, which is required by these rules to be provided with fire pumps operated by power such fire pumps (other than any emergency fire pump) shall together be capable of delivering for the fire fighting purposes a quantity of water, under the conditions and at the pressure specified in sub-rule (2) which shall not be less than the quantity obtained from the following formula :-

Quantity of water is cubic metres per hour = Cd2 where :

(a)        C=5 for ships required to be provided with more than one fire pump (excluding any emergency fire pump) and C=2.5 for ships required to be provided with only one fire pump, and

(b)        d=1+0.066 √ L(B+D) to the nearest 0.25 where

L=        length of the ship in metres on the summer load water line from the foresaid of the stem to the aferside of the rudder post.  Where there is no rudder post, the length is measured from the foreside of the stem to the axis of the rudder stock if that be the greater :

B=        greatest moulded breadth of the ship in metres; and

D=        moulded depth of the ship in metres measured to the bulkhead deck amidships:

Provided that in any such ship the total capacity of the fire pumps for fire fighting shall not be required to exceed 180 cubic metres per hour.

(c) (i)     In every ship which is required by these rules to be provided with more than one fire pump operated by power (other than any emergency fire pump) every such fire pump shall have a capacity of not less than 80 per cent of the total capacity of the fire pumps required by clause (b) of sub-rule (1) divided by the minimum number of fire pumps required by these rules to be provided in the ship but in any case not less than 25M3/hour.

(ii)      If more fire pumps operated by power than are required by these rules, are provided in any ship the Chief Surveyor with the Govt. of India may permit the capacity of any such additional fire pumps to be less than 80 per cent of the total required capacity divided by the minimum number of required pumps, but not less than 25M3/hours.

(iii)      Every fire pump which is operated by power (other than any emergency fire pump) shall be capable of producing from any fire hydrant or hydrants in the ship, at least the minimum number of jets of water required by these rules as appropriate to the class and tonnage of the ship, while maintaining the pressure required by sub-rule (2).

(iv)        In any ship in which automatic and remote control systems have been provided in the machinery space in lieu of continuous meaning of the space, arrangements shall be made to ensure immediate availability of water supply from the firemain at the required pressure either by permanent pressurization or by suitably placed remote starting of the fire pump.

(v)         Relief valves shall be provided in conjunction with all then fire pumps if the pumps are capable of developing a pressure exceeding the design pressure of fire main, water service pipes, hydrants or hoses provided that such valves shall be so placed and adjusted as to prevent excessive pressure in any part of the fire main system.

(vi)        Every centrifugal pump which is connected to the fire main shall be fitted with a non-return valve.

(viii)       In every ship of class I, II, III or IV an emergency fire pump shall be  fitted abatt of the ship's collision bulkhead.

(2)        Any fire pump shall, when discharging the quantity of water required by sub-rule (1) of rule 59 through adjacent fire hydrants in any part of the ship from nozzles of sizes specified in rule 61 be capable of maintaining the following pressure at any hydrant :

(a)        in any passenger ship.

(i)         of 4,000 tons and upwards :

3.1. bar (0.31 N/mm2)

(ii)         of 1,000 tons and upwards but under 4,000 tons :

2.7 bar (0.27 N/mm2)

(iii)        of under 1,000 tons :

2.1 bar (0.21 N/mm2)

(b)        in any ship other than a passenger ship.

(i)         of 6,000 tons and upwards :

2.7 bar (.027 N/mm2)

(ii)         of 1,000 tons and upward but under 6,000 tons:

2.5 bar (0.25 N/mm2)

(iii)        of under 1,000 tons :

2.1 bar (0.2) N/mm2)

Provided that the maximum pressure at any hydrant shall not exceed that at which the effective control of a fire hose can be demonstrated.

(3)        Emergency fire pumps shall be of approved type.  They shall be fixed, self printing and independently driven type which shall be capable of supplying two jets of water.  The capacity of the pump shall not be less than 40 per cent of the total capacity of all the fire pumps required by these rules and in any case not less than 25M3/hour whilst maintaining a minimum pressure of 2.5 bar (.25 N/mm2). The total suction head of the pump shall not exceed 4.5 M under all conditions of list and trim likely to be encountered in service and the suction piping shall be designed to minimize the suction losses.  The source of power of the pump and its location shall comply with the following requirements:-

(i)         Any diesel driven power source for the pump shall be capable of being readily started in its cold condition down to a temperature of 00C by hand cranking.  If this is impracticable, or if lower temperature are likely to be encountered, consideration is to be given to the provision and maintenance of heating arrangements, as may be approved by the Chief Surveyor with the Government of India, so that ready starting will be assured.  If hand cranking is impracticable, the Chief Surveyor with the Government of India may permit other means of starting, which shall be such as to enable the diesel driven power source to be started at least 6 times within a period of 30 minutes, and atleast twice within the first 30 minutes.  Any service fuel tank shall contain sufficient fuel to enable the pump to run on full load for atleast 3 hours and sufficient reserves of fuel shall be available outside the main machinery space to enable the pump to be run on full load for an additional 15 hours.

(ii)         Handle for starting the emergency fire pump prime mover should be stowed and marked so that it can be easily located in an emergency.

(iii)        There shall be no direct access between the machinery space and the space containing the emergency fire pump and its source of power.  When this is impracticable, an arrangement where the access is by means of an airlock, each of the two doors being self-closing, or through a water-tight door capable of being operated from a space remote from the machinery space and the pace containing the emergency fire pump and unlikely to be cut off in the event of fire in those spaces may be approved.  In such cases a second means of access to the space containing the emergency fire pump and its source of power shall be provided.

(iv)        Ventilation arrangements to the space containing the independent source of power for the emergency fire pump shall be such as to preclude, as far as, practicable, the possibility of smoke from a machinery space fire entering or being drawn into that space.

(4)        In cargo ship where other pumps, such as general service, bilge and ballast, etc. are fitted in a machinery space, arrangements shall be made to ensure that at least one of these pumps having the capacity and pressure required under sub-rule (1) (b) and sub-rule (2) is capable of providing water to the fire main.

## 59. FIRE MAIN, WATER SERVICE PIPES AND HYDRANTS.—

All water pipes and fire hydrants required to be provided under these rules shall be so placed that in addition to complying with other requirements specified in those rules, fire hoses may easily be coupled to them.

(1) In every ship which is required to be provided with fire pumps operated by power the diameter of the fire main and of the water service pipes connecting the hydrants thereto shall be sufficient for the effective distribution of the maximum discharge required by these rule from :

(a) where only one pump is required that pump, or

(b) where two such pumps are required, both pumps operating simultaneously, or

(c) where more than two such pumps are required, the two targest of such pumps operating simultaneously :

Provided that in any ship other than a passenger ship the diameter of the fire main and of the water service pipes shall be sufficient only for the discharge of 140 cubic metres per hour.

(2) In ships carrying deck cargo, the position of the hydrants shall be such that they are always readily accessible with pipes and arranged in a manner to avoid risk of damage from such cargo and in ships where the deck pipe lines rune on exposed deck, two such lines shall be provided.

(3) Water pipes shall not be made of material which may be readily rendered ineffective by heat.  They shall not be made of cast iron and if made of cast iron or steel, shall be galvanised or the pipe wall thickness shall be increased by a corrosion allowance.

(4) The fire hydrants shall be so placed that the fire hoses may be easily coupled to them.

(5) Isolating valves to separate the section of the fire main within the machinery spaces containing the main fire pump or pumps from the rest of the fire main shall be fitted in an easily accessible and tenable position outside the machinery spaces.  The fire main shall be so arranged that when the isolating valves are shut all the hydrants on the ship, except those in the machinery space, can be supplied with water by a fire pump not located in the machinery space through pipes which do not enter such space.  Where the machinery space is situated a midships the isolating valves shall also be provided in the fire main so that fire hydrants at both ends of the ship may be used simultaneously and separately.  Provided that in exceptional cases short lengths of the emergency fire pump suction and discharge piping to penetrate the machinery may be approved if it is impracticable to route it externally and that the integrity of the fire main is maintained by the enclosures of the piping in a substantial steel casing

(6) Hydrants valve of screw lift type or cocks shall be fitted to water service pipes and shall be so arranged that any fire hose coupled these to may be removed while fire pumps are in operation.

(7) All water pipes for fire extinguishing system shall be provided with drain valves or cocks for use in frosty weather and so located that they may not be damaged by cargo.

(8) Unless one hose and nozzles is provided for each hydrant in the ship be complete interchangeability of hose couplings and nozzles.

(9) In tankers isolation valves shall be fitted in the fire main at poop front in a protected position and on the tank deck at internals of not more than 40m. to preserve the integrity of the fire main system in case of fire or explosition.

(10) (a)number and position of hydrants shall be such that at least two jets of water not emanating from the same hydrant, one of which shall be from a single length of hose, may reach any part of the ship normally accessible to the passengers on crew while the ship is being navigated and any part of any cargo space when empty any ro/ro cargo space or any special category space in which latter case the two jets shall reach any part of such space each from a single length of hose.  Furthermore, such hydrants shall be position and near the access to the protected spaces.

(b)     Where any ship is required to provide one jet of water under the conditions required by these rules, hydrants sufficient in number shall be so positioned as to enable one jet of water from a single length of hose to reach any part of the ship normally accessible to the passengers or crew while the ship is being navigated, any store room and any part of any cargo space when empty.

(c)       In the accommodation service and machinery spaces of passenger ships the number and position of hydrants shall be such that the requirement of clause (a) and (b) are complied with when all water tight doors and all doors in main vertical zone bulk-heads are closed.

## 60.FIRE HOSES:-

(1) Fire hoses required to be provided under these rules shall not exceed 18 metres in length in ships having 9 moulded breadth of 27 metre or more, where the length of fie hoses for exterior locations and for cargo spaces shall not exceed 27 meters in length, which shall be made of closely woven flax canvas or other approved material and shall be provided with couplings, branchpipe and other necessary fittings, and with plain nozzles or dual-purposes nozzles.

(2) Every such fire hose together with the tools and fittings shall be kept in a conspicuous position near the hydrants or connection with which it is intended to be used.  In interior locations in passenger ship,  fire hoses shall be connected to the hydrants at all times.  Hose diameter shall be not loss than 64 millimetres if unlined or 45 millimetres if lined provided that the Chief Surveyor with the Government of India may permit smaller diameter hoses in ships of less than 500 tons.

(3) Such hose provided in compliance with these rules shall not be used for any purpose other than for extinguishing fire or testing with fire appliances at fire drill and surveys.

(4) In interior locations in passenger ship, carrying more than 36 passengers fire hoses shall be connected to hydrants at all times.

## 61. NOZZLES :--

(1) Every ship which is required under these rules to be provided with fire pumps operated by power shall be provided with nozzle of 12 millimetre, 16 millimetres, 19 millimetres in diameter or as near thereto in diameter as possible.  Nozzles larger in diameter may be provided if the requirements of these rules relating to the provision of water for fire fighting purposes are otherwise complied with.

(2) For machinery spaces and exterior location the diameter of the nozzles shall be such as to obtain the maximum possible discharge from the minimum number of jets of water and at the pressure required under these rules from the smallest fire pump permitted by clause (c) (1) of sub-rule 1 of rule 58 provided that the diameter of the nozzles shall not be greater than 19 millimetres.

(3) For accommodation and service space the diameter of the nozzles shall not be required to be greater than 12 millimetres.

(4) Every such nozzle shall be capable of producing a water spray suitable for extinguishing oil fires and a plain water jet and shall incorporate a shut-off facility.

62. LOCATION AND ARRANGEMENTS OF WATER PUMPS FOR OTHER FIRE EXTINGUISHING SYSTEMS:-

Pumps required for the provision of water for  other fire extinguishing systems required by these rules, their sources of power and their controls shall be installed outside the space or spaces protected by such systems and shall be so arranged that a fire in the pace or spaces protected will not put any such system out of action.

## 63. FIRE EXTINGUISHERS:-

(1) Non portable foam, carbon dioxide and dry powder fire extinguishers provided in compliance with these rules shall be constructed in accordance with the requirements specified in Schedules II, III and IV respectively.

(2)(a)     Portable fire extinguishers (other than carbon dioxide and dry powder fire extinguishers) provided in compliance with these rules shall, if they are of a type discharging fluid have a capacity of not more than 13.5 litres and not less than 9 litres;

(b)     Portable carbon dioxide fire extinguisher provided in compliance with these rules shall have a capacity of not less than 4.5 kg. of carbon dioxide;

(c)     Portable dry powder fire extinguishers provided in compliance with these rules shall have a capacity of not les than 4.5 kg.  of dry powder;

(3) Portable halogenated hydro-carbon fire extinguishers provided in compliance with these rules shall,--

(a)     have capacity of not less than 7 kilogrammes of halogenated hydrocarbon;

(b)     use either bromochlorodifluoromethane (B.C.F.)/ (Halon 1211) or bromotrifluoromethane (B.T.M.)/ (Halon 1301) as the extinguishing medium.

(4) Portable fire extinguishers of other than those specified in sub-rule (2) and (3) provided in compliance with these rules shall  be of not less than the fire extinguishing equivalent of 9 litres fluid extinguishers.

(5) Portable fire extinguishers provided in compliance with these rules.--

(a)     shall not exceed 25.5 kg. in weight in the fully charged condition and shall be as portable as a 13.5 litres fluid fire extinguisher;

(b)     for use in accommodation or service spaces of any ship, shall so far as practicable have a uniform method of operation;

(6) Fire extinguishers in which the substance used for extinguishing fire is stored under pressure shall not be provided for use in accommodation spaces :

Provided that portable dry power fire extinguishers may be provided in compliance with these rules in the accommodation spaces, service spaces or in the machinery spaces, subject to their number not exceeding one half of the total number of extinguishers required to be provided in each of these spaces.

(7) Fire extinguishers provided for use in any ship to which these rules apply shall not contain an extinguishing medium which either itself or when in use gives of gases harmful to persons.

(8) For the purposes of these rules,--

(a) the capacity of any fire extinguisher other than a carbon dioxide or halogenated fire extinguisher shall be taken to be the greatest volume or weight of extinguishing medium which it can contain when sufficient space is left to ensure the proper operation of the extinguishers;

(b) the capacity of carbon dioxide or halogenated hydrocarbon fire extinguisher shall be taken to be the greatest weight of carbon dioxide or halogenated hydrocarbon respectively which it can safely contain in a tropical climate.

(9) Portable carbon dioxide and halogenated hydrocarbon extinguishers shall not be located in accommodation spaces:

Provided that where such extinguishers are provided in compliance with these rules in radio rooms, at switch-boards and other similar positions, the volume of any space containing one or more extinguishers shall be such as to limit the concentration of vapour that can occur due to discharge, to not more than 5 per cent of the net volume of the space.

Explanation:--For the purpose of this rule, the volume of carbon dioxide shall be calculated at 0.56 Meter/kilogramme the volume of Halon 1301 at 0.16 meter3) kilogramme and the volume of Halon 1211 at 0.14 meter3/kilogramme.

(10) Where portable halogenated fire extinguishers are provided in compliance with these rules in machinery spaces, their number shall not exceed one half of the total number of extinguishers provided in such spaces.

(11) Fire extinguishers shall be periodically inspected at intervals not exceeding two years.

(12)       Every fire extinguishers provided in compliance with these rules shall be kept fully charged at all times.

(13)       A spare charge shall be provided for every portable fire extinguisher provided in compliance with these rules except that for each such fire extinguisher which is of a type that cannot readily be re-charged, while  the ship is at sea, an additional portable fire extinguisher of the same type, or its equivalent, shall be provided in lieu of a spare charge.

(14)       Acceptable equivalent for fire extinguishers-Whenever these rules provide for substitutes the acceptable equivalents for fire extinguishers shall be as prescribed below w :-

Froth     Carbon dioxide

136 litres45 kilogrammes

45 litres 16 kilogrammes

Portable  4.5 kilogrammes

## 64. FIRE BUCKETS :-

(1) Every fire bucket provided in compliance with these rules shall be painted red and shall be clearly and permanently marked in black or white with the word "FIRE".  Every such fire bucket shall be kept filled with sand or water.

(2) At least half the number of such fire buckets shall be fitted with lanyards of sufficient length to enable the buckets to be fitted from the sea with the ship in light condition.

(3) Such fire buckets shall not be used for any purpose other than for extinguishing fires.

## 65. SPECIAL REQUIREMENTS FOR FIXED FIRE EXTINGUISHING SYSTEMS :--

(1) Where halogenated hydrocarbon is used as all extinguishing medium in fixed fire extinguishing systems in accordance with these rules, its use shall be permitted only in machinery spaces, pump rooms and in cargo spaces intended solely for the carriage of vehicles which are not carrying any cargo.

(2) Where a fixed pressure water spraying system is used for the protection of special category spaces, cargo spaces where permitted by these rules or ro/ro cargo spaces, special consideration shall be given to the bilge pumping and drainage arrangements where such spaces are below the bulk-head deck and to the scupper arrangements where such spaces are above the bulkhead deck.

## 66. FIXED LOW-EXPANSION FOAM FIRE EXTINGUISHING SYSTEMS IN MACHINERY SPACES FITTED IN ADDITION TO REQUIREMENTS OF THESE RULES:-

(1) Where in any machinery space a fixed low-expansion foam fire extinguishing system is fitted in addition to the requirements of these rules, such system shall be capable of discharging through fixed discharge outlets in not more than five minutes a quantity of foam sufficient to cover to a depth of 150 mm the largest single area over which oil fuel is liable to spread.  The system shall be capable of generating foam suitable for extinguishing oil fires.  Means shall be provided for effective distribution of the foam through a permanent system of piping and control valves or cocks to suitable discharge outlets, and for the foam to be effectively directed by fixed sprayers on other main fire hazards in the protected space.  The expansion ratio of the foam shall not exceed 12 to 1.

(2) The means of control of any such system shall be readily accessible and be simple to operate and shall be grouped together in as few locations as possible at positions not likely to be cut off by a fire in the protected space.

## 67. FIXED FIRE EXTINGUISHING SYSTEMS NOT REQUIRED BY THESE RULES:-

In every ship where a fixed fire extinguishing system not required under these rules is provided, such a system shall be of the approved type and shall be installed outside the space or spaces protected by such systems and shall be so arranged that a fire in the space or spaces protected will not put any such system out of action.

## 68. FIRE CONTROL PLAN:

(1) There shall be permanently exhibited for the guidance of the master and officers of all ships over 20 metres in length, general arrangement plans showing clearly for each deck the position of the control station, the sections of the ship which are enclosed by fire resisting bulkheads, together with particulars of the fire alarms, fire detection systems, the sprinkler installations, fireman's outfits, fire extinguishing appliances, the means of access to the various compartments and decks in the ship, the ventilating system including particulars of the master-fan controls, the position of dampers and identification numbers of the ventilating fans serving each section of the ship, the location of the international shore connection, and the position of all means of control referred to in rule 69.

(2) The general arrangement plans required by this rule shall be kept up-to-date, any alteration being recorded therein without delay.

(3) In all ships a duplicate set of fire control plans or booklet containing such plans shall be permanently stored in a prominently marked weathertight enclosure outside the deckhouse for the assistance of shoreside fire fighting personnel.

(4) The Fire Control Plan shall include means of escape calculations, showing stair/door width determination, refuge capacity, and assembly station loads, as required by FSS Ch. 13.2.5.

## 69. MEANS FOR STOPPING MACHINERY, SHUTTING OFF OIL FUEL SUCTION PIPES AND CLOSING OF OPENINGS:

(1) In every ship to which these rules apply, there shall be provided :-

(a) means for stopping ventilation fans serving machinery, accommodation and cargo spaces ;

(b) means for closing all skylights, doorways, ventilators, annular spaces, around funnels and other openings to such spaces; and

(c) means to permit the release of smoke from machinery spaces.

(2) Such means shall be capable of being operated from positions outside the said spaces and which would not be made in accessible by a fire within such spaces.

(3) Machinery driving the forced and induced draught fane,  oil fuel transfer pumps, oil fuel unit pumps and other similar fuel pumps shall be fitted with remote controls situated outside the spaces in which such machinery or pumps are situated and which would not be made inaccessible by a fire within such spaces.  The controls shall be capable of stopping such machinery or pumps in the event of fire in such spaces.  For machinery spaces in passenger ships such controls together with the controls required in sub-rule (1) shall be situated at one control position or grouped is an few positions as possible.  Such controls shall have safe access from the open deck.

(4) Except as provided in sub-rule (5) in every ship to which these rules apply, every pipe connected to any oil fuel or lubricating oil storage, setting, or daily service tank, not being a double bottom tank, which if damaged would permit discharge of the contents so as to cause a fire hazard, shall be fitted with a valve or cock which shall be secured to the capable of being closed from a readily accessible position outside the space in which the tank is situated.

Provided that --

(a) in the case of any inlet pipe to such a tank, a non-return valve secured to the tank may be substituted,

(b) in the case of an oil fuel or lubricating oil deep tank situated in or adjacent to a shaft or pipe tunnel or similar space, a valve or valves (additional to the valve required to be fitted on the tank) may be fitted on the pipe line outside the tunnel or tunnels or similar space to enable control to be exercised in the event of fire.  Such valves if fitted in the machinery space shall be operated from a position outside the space.

(5) The valve or cock required under sub-rule (4) may be dispensed with in the case of a pipe connected to a lubricating oil tank fitted is a space other than a machinery space of category 'A' provided that the safety of the ship is not impaired.

## 70. AVAILABILITY OF FIRE FIGHTING APPLIANCES:

Fire appliances carried in any ship to which these rules apply shall be maintained in good order and shall be kept available for immediate use at all times.  All moveable fire appliances, other than firemen's outfits carried in compliance with these rules shall be stowed where they will be readily accessible from the spaces in which they are intended to be used and in particular one of the portable fire extinguishers intended for the use in any space shall be stowed near the entrance to that space.

All fire-fighting systems and appliances shall be tested at intervals prescribed in MSC.1/Circ.1432 (2012). Each ship shall maintain a Fire Safety Operational Booklet detailing test procedures, record logs, and crew training certificates.

## 71. APPROVAL OF MATERIAL :

Where these rules require that a particular fitting, appliance, apparatus or equipment or any type or equivalent thereof shall be provided, fitted or carried or any particular arrangement or provision shall be made, then every such fitting, appliances apparatus or equivalent thereof or any such arrangement or provision shall be such as is reasonably adequate for the purpose for which it is required to be provided.

## 72. SPACES CONTAINING PARTICULAR RISKS:

In every ship to which these rules apply containing spaces such as galleys, gasoling compartments, cinemas, electric-steering gear, battery charging room and such other similar spaces which in the opinion of the Director General of Shipping or Chief Surveyor with the Government of India contain particular risk, there shall be provided such additional fire appliances as may be specified by them.

## 73. REQUIREMENTS FOR SHIPS OF SPECIAL DESIGN AND LAYOUT:-

Where in the case of a ship in which particular fittings, appliances, apparatus or any other equipment or any type thereof, fitted in compliance with these rules are not considered by the Director General of Shipping as adequate, having regard to her design, layout or susceptibility to risk of fire, it may, notwithstanding anything contained in these rules, require, by order in writing the ship to be provided such other fittings, appliances, apparatus or equipment as it may consider necessary.

## 74. EQUIVALENTS, EXEMPTIONS AND SAVING:-

(1) Where these rules require that a particular fitting material, appliance, apparatus, equipment, or any type thereof shall be fitted or carried in a ship or that any particular arrangement or provision shall be made, the Chief Surveyor with the Government of India may in writing allow any other fitting material, appliance, apparatus or any type thereof to be carried or fitted or any other arrangement or provision to be made in that ship if he is satisfied by trial thereof or otherwise, that such other fittings, materials, appliance, apparatus, equipment or type thereof or any such other arrangement or provision is at least as effective as that required under these rules.

(2) The Director General of Shipping or Chief Surveyor with the Govt. of India may :-

(i)  exempt, in writing, any ship from the requirements o these rules if he is satisfied that by the nature of her construction and design, it is neither practicable nor reasonable for that ship to comply with such requirements on such conditions as he thinks fit.

(ii)  exempt in writing, any ship which is not normally engaged on international voyages but which in exceptional circumstances is required to undertake a single international voyage from the requirement of these rule, provided the ship complies with such safety requirements as are, in the opinion of the Director General of Shipping, or as the case may be the Chief Surveyor with the Government of India, adequate for the intended voyage.

## 75. PENALTIES :-

Whoever commits a breach of any of the provision of these rules shall be punishable with a fine which may extend to rupees on thousand and in the event of a continuing breach of these rules, with a further fine of rupees fifty for every day after the first day which the breach continues.

## 76. Procedures, Forms & Authority for Survey

The procedures, forms, and authority for the survey, approval, and certification of fire appliances shall, as far as applicable, conform to the provisions of the Merchant Shipping (Life Saving Appliances) Rules, XXXX and the Merchant Shipping (Safety Convention Certificates) Rules, XXXX

# SCHEDULE I

(See rules 14, 23 and 36)

INTERNATIONAL SHORE CONNECTION

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(1)        The international shore connection, shall be in accordance with the following specifications:-

Outside diameter 178 millimetres

Innner diameter     64 millimetres

Blot circle diameter         132 millimetres

Holes    4 holes each of 19 millimetres diameter equidistantly placed slotted to the flange periphery.

Flange thickness           14.5 millimetres minimum

Bolts     4, each of 16 millimetres diameter. 50 millimetre in length with washers.

Flange surface   Flat face

Material Any suited to 10 bar (1.0 N/mm2) service.

Gasket  Any suited to 10 bar (1.0 N/mm2) service.

_____________________________________________________________

(2)        The connection shall be constructed of material suitable for 10 bar (1.0 N/mm2 service.  The flange shall have a flat face on one side, and to the other shall have permanently attached there to a coupling that will fit the ship's hydrants and hoses.  The connection shall be kept aboard the ship together with the gasket, four 16 millimetres bolts, 0 millimetres in length and eight washers.

# SCHEDULE –II

( See rule 63)

NON-PORTABLE FOAM FIRE EXTINGUISHERS.

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(1)        Every foam fire extinguisher, other than a portable fire extinguisher provided in compliance with these rules shall  be constructed in accordance with approved specifications and be of suitable materials and shall be of sufficient strength to withstand with an adequate factor of safety the maximum internal pressure to which it may be subjected and shall be capable of withstanding a test by hydraulic pressure, in excess of the maximum working pressure.  Fore the purpose of this schedule the maximum working pressure shall be the equilibrium pressure that develops within the body at 700C when the correctly charged extinguisher has been operated with all outlets closed.  The interior of the extinguisher shall be capable of being examined.

(2)        The body of the extinguisher shall be cylindrical with ends which shall be dished outwards without reverse flanging to a radius not exceeding the diameter of the body.  The body and ends shall be made of sheet steel which shall be tinned on lead-coated internally, and every part of the extinguisher shall, where necessary, be protected against corrosion.  The body of the extinguisher shall be welded.

(3)        Where the extinguisher is provided with a gas cylinder as the means for expelling the extinguishing medium, such gas cylinder shall be constructed to approve specifications.

(4)        The extinguisher shall be provided with an opening for the introduction of an inner container which shall be adequately supported.  The opening shall be fitted with a cap of gun-metal or other suitable materials, screwed with a continuous thread, through the side of which safety holes or slots shall be provided so that when the cap is being removed any pressure of gas remaining in the container may be released gradually, should the discharge opening be choked.  [The cap joint shall be made with acid-resisting rubber, greased leather, or other suitable material.  The extinguisher shall have the correct filling level clearly indicated.  The design shall permit the ready availability of the extinguisher to be verified as required and ensure that it will be apparent whether or not the extinguisher has been operated.

(5)        The extinguisher shall be provided with a controllable device to enable the discharge to be interrupted and means to prevent the loss of liquid when the extinguisher is standing.

(6)        The extinguisher actuating mechanism shall be protected so that it is safeguarded against inadvertent operation.

(7)        A reinforced discharge hose shall be provided together with a nozzle, the area of which shall be such that when the extinguisher is operated, the foam is projected to a distance of 14.0 metres for a period not less than 90 seconds, in the case of an extinguisher of 135 litres capacity or over and to distance of 10.0 metres for a period not less than 60 seconds in the case of an extinguisher of under 135 litres capacity.  The nozzle and the reinforced discharge hose should be capable to withstand four times the maximum working pressure specified in para (1) of this schedule.

(8)        The charge and the air space above the level of the solution in the body shall be so regulated tha the maximum pressure in the extinguisher when put into action, with all outlets closed, does not exceed 19.50 bar 1.95 N/mm2 with solution at a temperature of 380C.

(9)        The extinguisher shall be capable of withstanding for a period of 5 minutes an internal pressure of 1-1/2 times the maximum working pressure specified in para (1) of this schedule, in the extinguisher when put into action with all outlets closed, and in no event of less than 24.5 bar (2.45 N/mm2).

(10)       The outside of the extinguisher; shall be clearly and permanently marked with :-

(a)        the name of the maker or vendor of the extinguisher;

(b)        the capacity of the extinguisher;

(c)        the pressure under which the extinguisher was tested;

(d)        instructions for operating the extinguisher;

(e)        the year in which the extinguisher was manufactured;

(f)         the level of the solution, when the extinguisher is filled to its working capacity.

# Schedule IIA

Fire Integrity Ratings

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(See rule 6A)

Bulkheads and decks shall be constructed to fire-resistance standards not less than those stipulated for A-, B- or C-Class divisions under FSS Code Chapter 3 and SOLAS Regulation II-2/9. A-60 divisions shall resist fire for 60 minutes; B-15 divisions for 15 minutes; temperature rise limitations shall not exceed 140 °C on average and 180 °C at any point.

# SCHEDULE – III

(See rule 63)

Non-Portable Carbon Dioxide fire extinguishers

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(1)     Every carbon dioxide fire extinguisher provided in compliance with these rules shall be provided and constructed in accordance with approved specifications.

(2)     Each cylinder shall be provided with an internal discharge tube, and a valve to release the gas.

(3)        The extinguisher shall be provided with a discharge hose which shall be reinforced so as to withstand a pressure of at least 122 bar (12.2 N/mm2) when the necessary couplings are fitted.  The bore of the discharge hose shall not be less than the sizes respectively set forth in the following table :-

Capacity of extinguisher Period

_____________________________________________________________

16.0 Kg.30 to 45 seconds

45.0 Kg.60 to 90 seconds

____________________________________________________________

(5)        The outside of the extinguisher shall be clearly and permanently marked with :-

(a)        the name of the maker or vendor of the extinguisher;

(b)        the capacity of the extinguisher;

(c)        instructions for operating the extinguisher;

(d)        markings which will indicate the respective weights of the extinguisher when empty and when filled;

(e)        the year in which the extinguisher was factured.

(f)         the pressure under which the extinguisher was being hydraulically tested.

# SCHEDULE - IV

(See rule 63)

Non-Portable Dry Powder Fire Extinguishers:

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(1)        Every dry powder fire extinguisher, other than a portable fire extinguisher, provided in compliance with these rule shall be constructed of suitable materials and shall be of an efficient design and of sufficient strength to withstand with an adequate factor of safety the maximum internal pressure to which it may be subjected and shall be capable of withstanding a test by hydraulic pressure suitably in excess of the maximum working pressure.  For the purpose of this schedule, the maximum working pressure shall be the equilibrium pressure that develops within the body at 700C when the correctly charged extinguisher has been operated with all outlets closed.

(2)        Where the extinguisher is provided with a gas cylinder as the means for expelling the extinguishing medium, such gas cylinder shall be in accordance with approved specifications.

(3)        The extinguisher shall be provided with a nozzle and a reinforced discharge hose constructed to withstand four times the maximum working pressure specified in para (1) of this schedule.

(4)        Any necessary openings in the extinguisher body shall be fitted with caps or covers so designed that any pressure remaining in the container may be released gradually before the cap or cover can be removed completely.

(5)        Every part of the extinguisher shall, where necessary, be protected against corrosion.

(6)        The extinguisher shall be effectively sealed to present the ingress of moisture, but such sealing arrangements shall not interfere with the discharge of the extinguisher.

(7)        The extinguisher shall be provided with a controllable device to enable the discharge to be interrupted.

(8)        The extinguisher actuating mechanism shall be protected so that it is safeguarded against inadvertent operation.

(9)        The design shall permit the ready availability of the extinguisher to be verified as required and ensure that it will be apparent whether or not the extinguisher has been operated.

(10)       A fully charged extinguisher shall, when operated under normal conditions, be capable of discharging not less than 85 per cent of the mass of the dry power charge.  The discharge rate shall be not less than 1 kilogramme per second.

(11)       The outside of the extinguisher body shall be clearly marked with :--

(a)        name of the maker or vendor of the extinguisher;

(b)        the capacity of the extinguisher;

(c)        the pressure under which the extinguisher was tested ;

(d)        instructions for operating the extinguisher ;

(e)        the year in which the extinguisher was manufactured.

# SCHEDULE – V

[See rule 7(1)(ii), 10(2)(a), 10(3)(ii), 29(b)(ii), 30(2) and (3)]

Portable Foam Applicator Units :

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(1)        Every portable foam applicator unit provided in compliance with these rules shall be provided with :-

(a)        an induction type of air-foam nozzle capable of being connected to the fire main by means of a fire hose;

(b)        a portable tank containing at least 20 litres of form concentrate from which the nozzle specified at sub-para (a) of this paragraph can induce the contents;

(c)        a spare tank identical to that specified at sub-para (b) of this paragraph.

(2)        The nozzle whilst being supplied at the minimum hydrant pressure on the ship permitted by these rules shall be capable of producing effective foam suitable for extinguishing an oil fire at the rate of at least 1.5 cubic metres per minute.

(3)        The foam expansion ratio (i.e the ratio of the volume of foam produced to the volume of foam solution) shall not exceed 12 to 1.

(4) Portable fire extinguishers shall be approved per IMO Res. A.951(23), constructed of corrosion-resistant materials, mass ≤ 23 kg, and exclude Halon agents. Each unit shall carry a fire-rating mark indicating minimum Class A or B capacity.

# SCHEDULE - VI

[See rules 15, 22, 35, 37(2)(i) and 52]

Fireman's Outfit:

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(1)        Every fire man's outfit shall be constructed in accordance with approved specifications and consist of the following :

(a)        Personal equipment.

(b)        A breathing apparatus of an approved type.

(c)        Fire proof life line of sufficient length and strength capable of being attached by means of a snap hock to the harness of the apparatus or to a separate belt in order to prevent the breathing apparatus becoming detached when life line is operated.

(2)        Personal equipment:-The personal equipment shall comprise the following namely :-

(a)        Protective clothing of material to protect the skin from the heat radiating from the fire and from burns and scalding from steam.  The outer surface shall be water resistant.

(b)        Boots and gloves of rubber or other electrically non-conducting material.

(c)        A rigid helmet providing effective protection against impact.

(d)        An electric safety lamp (hand lantern) of approved type with a minimum burning period of 3 hours.

(e)        An axe fitted with an insulated handle.

(3)        Breathing apparatus (Air Hose Type):-

Every smoke helmet or smoke mask shall be provided with a hose for the supply of air from the outside atmosphere.  An air pump or bellows shall be provided which shall be suitable for pumping air through the hose.  The hose shall be of the non-collapsing type and shall be sufficient in length to enable the air pump or bellows to be on the open deck in clean air, well clear of any hatch or doorway while the wearer of the helmet or mask is in any part of the accommodation, service, cargo or machinery spaces. Couplings shall be provided if two or more lengths of hose are to be joined in order to reach the aforesaid spaces.  The air inlet to the pump or bellows shall be so protected as to ensure that the supply of air is not obstructed.  If in order to comply with this subparagraph, an air hose exceeding 36 metres in length is necessary, a self-contained breathing apparatus shall be substituted or provided in addition.

(4)        Self-contained breathing apparatus :-- Every self-contained breathing apparatus shall :-

(a)        be of the open circuit compressed air type and shall be of a approved type;

(b)        be capable of functioning for at least 30 minutes and shall be provided with not m ore than one face mask unless the apparatus has been approved for use with a second face mask which may be used in emergency;

(c)        contain storage capacity of the compressed air cylinder or cylinders attached to the apparatus and carried by the weather of at least 1,200 litres of free air.  The storage cylinders shall be of sufficient strength and be capable of withstanding hydraulic pressure in excess of the maximum working pressure.

(d)        contain provision for automatic regulation of air supply to the wearer of the apparatus in accordance with his breathing requirements when he is breathing any volume of free air of up to 85 litres per minute at any time when the pressure in the supply cylinder or cylinders is above 10.5 bars (1.05 N/mm2). Means shall be provided for overriding the automatic air supply to increase the volume of aireavailable to the wearer if required.

(f)         not weigh more than 16 kilogrammes excluding any lifeline and if they do not foam an integral part of the apparatus, any safety belt or harness;

(g)        be provided with fully charged spare cylinders having a spare storage capacity of at least 2,400 litres of free air except where :

(i)         the ship is carrying five sets or more of such apparatus the total spare storage capacity of free air shall not be required to exceed 9,600 litres; or

(ii)         the ship is equipped with means for recharging the air cylinders to full pressure with air, free from contamination, the spare storage capacity of the fully charged spare cylinders of each such apparatus shall be of at least 1,200 litres of free air and the total spare storage capacity of free air provided in the ship shall not be required to exceed 4,800 litres

(h)        contain provision for warning the wearer audibly when 80 per cent of usable capacity of the apparatus has been consumed.

(i)         accompany a servicing and instruction manual.

(5)        General :- Every breathing apparatus shall--

(a)        be constructed of material having adequate mechanical strength and durability and be resistant to deterioration by heat, contact with water or to fire and shall not allow the breathing circuit to be penetrated by smoke or chemical fumes likely to be encountered in service.  The fabric used in the construction of any harness provided with such apparatus shall be resistant to shrinkage.  Exposed metal parts of the apparatus, harness and fittings shall be of materials, so far as practicable, resistant to frictional sparking.

(b)        accompany for use,

(i)         a fire-proof life and signaling line at least 3 metres longer than is required to reach from the open deck in clean air clear of any hatch or doorway to any part of the accommodation, service, cargo or machinery spaces.  Such line shall be made of copper or galvanized steel wire rope having a breaking strength of at least 500 kilogrammes and shall be overlaid up to at least 32 millimetres in circumference by hemp or other covering to provide a surface which can be firmly gripped when wet;

(ii)         an adjustable safety belt or harness to which such line shall be capable of being securely attached and detached by the wearer by means of a snaphook;

(iii)        provision for protecting the eyes and face of the wearer against smoke;

(iv)        plates of suitable non-flammable material bearing a clearly legible code of signals to be used between the wearer and his attendant, one of which shall be attached to the safety belt o rharnness and another attached to the free end of the life-line.

(c)        be clearly marked with the name of the maker or vendor and the year of manufacture;

(d)        contain operating instructions in clear and permanent lettering.

# SCHEDULE – VII

[See rule 5(iii), (iv) (v) and (vi), VII and 34(1), (2) and (3), 50(1)(a)]

FIXED FIRE DETECTION AND FIRE ALARM SYSTEMS

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(1)        General requirements.

(a)        Any required fixed fire detection and fire alarm system with manually operated call points shall be of approved type and capable of immediate operation at all times.

(b)        Power supplies and electric circuits necessary for operation of the system shall be monitored for loss of power or fault conditions as appropriate.  Occurrence of a fault condition shall initiate a visual and audible fault signal at the control panel which shall be distinct from a fire signal.

(c)        There shall be not less than two sources of power supply for the electrical equipment used in the operation of the fire detection and fire alarm system, one of which shall be an emergency source. The supply shall be provided by separate feeders reserved solely for that purpose.  Such feeders shall run  to an automatic change-over switch situated in or adjacent to the control panel for the fire detection system.

(d)        Detectors and manually operated call points shall be grouped into sections.  The activation of any detector or manually operated call points shall initiate a visual and audible fire signal at the control panel and indicating units.  If the signals have not received attention within two minutes an audible alarm shall be automatically sounded throughout the crew accommodation and service spaces, control stations and machinery spaces of category A.  This alarm sounder system need not be an integral part of the detection system.

(e)        The control panel shall be located on the navigating bridge or in the main fire control station.

(f)         Indicating units shall denote the section in which a detector or manually operated call point has operated.  At least one unit shall be so located that it is easily accessible to responsible members of the crew at all times, when at sea or in port except when the ship is out of service.  One indicating unit shall be located on the navigating bridge if the control panel is located in the main fire control station.

(g)        Clear information shall be displayed on or adjacent to each indicating unit about the spaces covered and the location of the sections.

(h)        No section covering more than one dock within accommodation spaces, service spaces and control stations shall be permitted except a section which covers an enclosed stairway.   In order to avoid delay in identifying the source of fire, each section shall contain not more than 100 detectors and shall cover not more than 50 rooms.

(i)         In passenger ship a section of detectors shall not serve spaces on both sides of the ship nor on more than one deck and neither shall it be situated in more than one main vertical zone except that the Chief Surveyor with the Government of India if he is satisfied that the protection of the ship against fire will not thereby be reduced, may permit such a section of detectors to serve both sides of the slup and more than one deck.

(j)         A section of fire detectors covering a control station, service space, accommodation space or cargo space shall not include a machinery space of category A.

(k)        Detectors shall be operated by heat, smoke or other products of combustion, flam or any combination of there factors.  Detectors operated by other factors, indicative of incipient fires may be accepted provided that they are no less sensitive than such detectors. Flame detectors shall be used only as additional to smoke or heat detectors.

(l)         Suitable instructions and spare components for testing and maintenance shall be provided.

(m)       The function of the detection system shall be periodically tested by means of equipment producing hot air at the appropriate temperature, or smoke or aerosol articles having the appropriate range of density or particle size, or other phenomona associated with incipient fires to which the detector is designed to respond.  All detectors shall be of a type such that they can be tested for correct operation and restored to normal surveillance without the renewal of any component.

(n)        The fire detection system shall not be used for any other purpose except that closing of fire doors and similar functions may be permitted at the control panel.

(2)        Installation requirements.

(a)        Manually operated call points shall be installed throughout the accommodation spaces, service spaces and control stations.   One manually operated call point shall  be located at each exit.  Manually operated call points shall be readily accessible in the corridors of each dock such that no part of the corridor is more than 20 meters from a manually operated call point.

(b)        Smoke detectors shall be installed in all stairways, corridors and escape routes within accommodation space.

(c)        Where a fixed fire detection and fire alarm system is required for the protection of spaces other than those specified in para (2)(a) of this schedule of least one detector complying with para (1)(k) of this schedule shall be installed in each such space.

(d)        Detectors shall be located for optimum performance.  Positions near beams and ventilation ducts or other positions where patterns of air flow could adversely affect performance and positions where impact or physical damage is likely shall be avoided.  In general, detectors which are located in overhead positions shall be a minimum distance of 0.5 metre away from bulkheads.

(e)        The maximum spacing of detectors shall be decided on the basis of characteristics of the detectors but, ordinarily shall be in accordance with the table below :-

Type of Maximum         Maximum          	Maximum
detectorfloor area         distance apart    distance
   per detector       between centersaway from
         	bulkheads

_____________________________________________________________

Heat     37m2   	   9m        		4.5 m

_____________________________________________________________

Smoke  74m2        11m      	5.5m

_____________________________________________________________

(f)         Electrical wiring which forms part of the system shall be so arranged as to avoid galleys, machinery spaces of category A, and other enclosed spaces of high fire risk except where it is necessary to provide for fire detection or fire alarm in such spaces or to connect to the appropriate power supply.

(3)        Design requirements :

(a)        The system and equipment shall be suitable designed to withstand supply voltage variation and transients, ambient temperature changes, vibration, humidity, shock, impact and corrosion normally encountered in ships.

(b)        Smoke detectors required by para (2)(b) shall be certified to operate before the smoke density exceeds 12.5 per cent, obscuration per metre, but not to operate until the smoke density exceeds 2 per cent, obscuration per metre.  Smoke detectors to be installed in other spaces shall operate within approved sensitivity limits having regard to the avoidance of detector insensitivity or over-sensitivity.

(c)        Heat detectors shall be certified to operate before the temperature exceeds 780 C but not to operate until the temperature exceeds 54 C.  when the temperature is raised to those limits at a rate less than 10C per minute.  At higher rates of temperature rise, the heat detector shall operate within approved temperature limits having regard to the avoidance of detector insensitivity or oversensitivity.

(d)        The permissible temperature of operation of heat detectors may be increased to 300C above the maximum deckhead temperature in drying rooms and similar spaces of a normal high ambient temperature.

(4)        Special requirements for periodically unattended machinery spaces.

For periodically unattended machinery spaces the fixed fire detection and fire alarm system shall comply with the following additional requirements :-

(a)        This fire detection system shall be so designed and the detectors so positioned as to detect rapidly the onset of fire in any part of those spaces and under any normal conditions of operation of the machinery and variations of ventilation as required by the possible range of ambient temperatures.  Except in spaces of restricted height and where their use is specially appropriate detection systems using only thermal detectors shall not be permitted.  The detection system shall initiate audible and visual alarms distinct in both respects from the alarms of any other system not indicating fire, in sufficient places to ensure that the alarms are heard and observed on the navigating bridge and by a responsible engineer officer.  When the navigating bridge is unmanned the alarm shall sound in a place where a responsible member of the crew is on duty.

(b)        After installation the system shall be tested under varying conditions of engine operation and ventilation.

(5)        Special requirements for cargo spaces.

In cargo spaces the system shall comply with the following additional requirements :-

(a)        Detectors shall be grouped into separate sections such that a section shall cover not more than one cargo space.  Each section shall contain not more than 100 detectors.

(b)        The type, number and spacing of detectors shall be to the satisfaction of the Chief Surveyor with the Govt. of India taking into account the conditions of ventilation and other factors prevailing in the space in which the detectors are installed.

(c)        In special category spaces and ro-ro cargo spaces, the system shall be capable of rapidly detecting the onset fire.  After being installed, the system shall be tested under normal ventilation conditions and shall give an overall response time to the satisfaction of the Chief Surveyor with the Government of India.

(6) Smoke detectors shall have sensitivity between 2–12.5 % obscuration per metre, individually addressable, with loop fault isolation and dual power supply. System design to conform to IEC 60092-504 and EN 54.

# SCHEDULE VIII

[See rules 5(v) and 34(3)]

SAMPLE EXTRACTION SMOKE DETECTION SYSTEMS

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(1)        General requirements.

(a)        Wherever in the text of this schedule the word "system" spears, it shall mean "sample extraction smoke detection system".

(b)        Any required system shall be capable of continuous operation, at all times except that systems operating on a sequential scanning principle may be accepted, provided that the interval between scanning the same position twice gives an overall response time to the satisfaction of the Chief Surveyor with the Govt. of India.

(c)        Power supplies necessary for the operation of the system shall be monitored for loss of power.  Occurrence of loss of power shall initiate a visual and audible signal at the control panel and the navigating bridge which shall be distinct from a signal indicating smoke detection.

(d)        An alternative power supply for the electrical equipment used in the operation of the system shall be provided.

(e)        The control panel shall be located on the navigating bridge or in the main fire control station.

(f)         The detection of smoke or other products of combustion shall initiate a visual and audible signal at the control panel and the navigating bridge.

(g)        Clear information shall be displayed on or adjacent to the control panel designating the spaces covered.

(h)        The sampling pipe arrangements shall be such that the location of the fire can be readily identified.

(i)         Suitable instructions and spare components shall be provided for the testing and maintenance of the system.

(j)         The function of the system shall be periodically tested to the satisfaction of the Chief Surveyor with the Govt. of India.  The system shall be of a type that can be tested for correct operation and restored to normal surveillance without the renewal of any component.

(k)        The system shall be designed constructed and installed so as to prevent the leakage of any toxic or flammable substances of fire extinguishing medium into any accommodation space, service space, control station or machinery space.

(2)        Installation requirements.

(a)        At least one smoke accumulator shall be located in every enclosed space for which smoke detection is required.  However, where space is designed to carry oil or refrigerated cargo alternatively with cargoes for which a smoke sampling system is required, means may be provided to isolate the smoke accumulators in such compartments for the system.  Such means shall be to the satisfaction of the Chief Surveyor with the Govt. of India.

(b)        Smoke accumulators shall be located for optimum performance and shall be spaced so that no part of the overhead deck area is more than 12 metres measured horizontally from an accumulator.  Where systems are used in space which may be mechanically ventilated, the position of the smoke accumulators shall be considered having regard to the effects of ventilation.

(c)        Smoke accumulators shall be positioned where impact or physical damage is unlikely to occur.

(d)        Not more than four accumulators shall be connected to each sampling point.

(e)        Smoke accumulators from more than one enclosed space shall not be connected to the same sampling point.

(f)         Sampling pipes shall be self-draining and suitably protected from impart or damage from cargo working.

(3)        Design requirements.

(a)        The system and equipment shall be suitable designed to withstand supply voltage variations and transients, ambient temperature changes, vibration, humidity, shock, impact and corrosion normally encountered in ships and to avoid the possibility of ignition of flammable gas/air mixtures.

(b)        The sensing unit shall be certificated to operate before the smoke density within the sensing chamber exceeds 6.65 per cent obscuration per metre.

(c)        Duplicate sample extraction fans shall be provided.  The fans shall be of sufficient capacity to operate with the normal conditions of ventilation in the protected area and shall give an overall response time to the satisfaction of the Chief Surveyor with the Govt. of India.

(d)        The control panel shall permit observation of smoke in the individual sampling pipe.

(e)        Means shall be provided to monitor the air flow through the sampling pipes and to ensure that as far as practicable equal quantities are extracted from each interconnected accumulator.

(f)         Sampling pipes shall be a minimum of 12 millimetres internal diameter except when used in conjunction with fixed gas fire extinguishing systems when the minimum size of pipe should be sufficient to permit the fire extinguishing gas to be discharge within the appropriate time.

(g)        Sampling pipes shall be provided with an arrangement for periodically purging with compressed air.

# SCHEDULE IX

[See Rules 8(1) and (2) (b), 10(1) (b), 27(1) (a), (2) and (3) 30(1) (b), 31(c), 37(2) (f), 41(2) (3)

Fixed Gas Fire Extinguishing Systems.

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(1)        General.

(a)        Fire extinguishing systems provided for use in any ship to which these rules apply shall not contain an extinguishing medium which not contain an extinguishing medium which either itself or under expected conditions of use gives off toxic gases in such quantities as to endanger personnel.

(b)(i)      In every such system provided for the injection of fire extinguishing medium into any compartment for fire extinguishing purposes, the pipes for conveying the medium shall be provided with control valves or cocks which shall be

be so placed that they will be easily accessible and not readily cut off from use by an outbreak of fire within the protected compartment.  Such control valves or cooks shall be permanently marked to indicate clearly the compartments to which the pipes are led.

(ii)      Where cargo spaces fitted with a gas extinguishing system for fire protection are used as passenger spaces the extinguishing connection shall be blanked during service as a passenger space.

(iii)     Suitable provisions shall be made to prevent inadvertent admission of the medium to any compartment.

(c)        The piping for the distribution of fire extinguishing medium shall be arranged and discharge nozzles so positioned that a uniform distribution of medium is obtained.

(d)        Means shall be provided to close all openings which may admit air to or allow gas to escape from a protected space.

(e)        Where the volume of free air contained in air receivers in any space in such that, if released in such space in the event of fire , such release of air within that space would seriously affect the efficiency of the fixed fire extinguishing system, an additional quantity of fire extinguishing medium shall be provided.

(f)         Means shall be provided for automatically giving audible warning of the release of fire extinguishing medium into any space in which personnel normally work or to which they have access.  The alarm shall operate for a suitable period before the medium is released.

(g)        The means of control of any fixed gas fire extinguishing system shall be readily accessible and simple to operate and shall be grouped together in as few locations as possible at positions not likely to be cut off by a fire in a protected space.  At each location there shall be clear instructions relating to the operation of the system having regard to the safety of personnel.

(h)        Automatic release of fire extinguishing medium shall not be permitted except as provided by sub-para (3)(c)(v) and in respect of local automatically operated units referred to in sub-para (3) (d) and (3)(e).

(i)         Where the quantity of extinguishing medium is required to protect more than one space, the quantity of medium available need not be more than the largest quantity required for any one space so protected.

(j)         Except as otherwise permitted by sub-para (3) (c), (3) (d) and (3) (e), pressure containers required for the storage of fire extinguishing medium shall be located out side protected spaces in accordance with sub-para (1) (a).

(k)        The storage containers and associated pressure components shall be constructed of suitable material and shall be of efficient design and sufficient strength having regard to their locations and maximum ambient temperatures expected in service.

(l)         When the fire extinguishing medium is stored outside a protected space, it shall be stored in a room which shall be situated in a safe and readily accessible position and shall be effectively ventilated.

Any entrance to such a storage room shall be from the open dock and in any case shall be independent of the protected space.  Access doors shall open outwards, and bulk-heads and decks including doors and other means of closing any opening therein, which form the boundaries between such rooms and adjoining enclosed spaces shall be gas tight.

(m)       Spare parts for the system shall be stored on board.

(2)        Carbon dioxide systems.

(a)        When carbon dioxide is used as the extinguishing medium in cargo spaces, the quantity of gas, available shall be sufficient to give a minimum volume of free gas equal to 30 per cent of the gross volume of the largest cargo compartment in the ship which is capable of being sealed.

(b)        When carbon dioxide is used as the extinguishing medium in cargo spaces containing motor vehicles with fuel in their tanks for their own propulsion or in closed ro/ro spaces or closed ro/ro spaces used for bulk stowage of cargo, the quantity of gas available shall be sufficient to give a minimum volume of free gas equal to 45 per cent of the gross volume of the largest such cargo space which is capable of being effectively sealed.

(c)        When carbon dioxide is used as an extinguishing medium for machinery spaces or pump rooms, the quantity of gas available shall be sufficient to give a minimum of free gas equal to the larger of the following quantities, either :

(i)         40 per cent of the gross volume of the largest space, such volume being measured upto the level at which the horizontal area of the casing is 40 per cent or less  of the gross area of such space measured midway between the tank top and the lowest part of the casing; or

(ii)         35 per cent, of the gross volume of the largest space including the casing;

Provided that the aforesaid percentages may be reduced to 35 per cent and 30 per cent respectively for ships of under 2,000 tons, not being passenger ships, provided also that if two or more machinery spaces are not entirely separate they shall be considered as forming one space.

(d)        The volume of carbon dioxide shall be calculated at 0.56 cubic metre per kilogramme.

(e)(i)      When carbon dioxide is used as the extinguishing medium for machinery spaces or pump rooms the arrangements shall be such that 85 per cent of the gas required to provide the concentration referred to in sub-para (2) (c) when applied to the space concerned can be discharged into that space within two minutes.

(ii)      When carbon dioxide is used as the extinguishing medium in cargo spaces containing motor vehicles with fuel in their tanks for their own propulsion or in closed ro/ro spaces the arrangements shall be such as to ensure that at least two thirds of the gas required for the space can be introduced within 10 minutes.

(f)         Safe means shall be provided for the crew to check the quantity of medium within the containers.

(3)        Halogenated hydrocarbon systems.

(a)        The use of halogenated hydrocarbons as fire extinguishing media is only permitted in machinery spaces, pumprooms and in cargo spaces intended solely for the carriage of vehicles which are not carrying any cargo.

(b)        When halogenated hydrocarbons are used as the fire extinguishing media in total flooding systems:

(i)         The system shall be arranged for manual initiation of power release only and such means shall be provided outside the protected space.

(ii)         Where the cargo of halogenated hydrocarbon is required to supply more than one space, the arrangements for its storage and release shall comply with sub-para (3) (b) (ix) or (3) (b) (x) for each such space.

(iii)        Means shall be provided for stopping automatically all ventilation fans serving the protected space before the medium is released.

(iv)        Means shall be provided to close manually all dampers in the ventilation system serving a protected space.

(v)         The arrangements shall be such that the liquid phase of the minimum quantity of medium required by sub-para (3) (b) (ix) or (3) (b) (x) when applied to the space concerned can be discharged into that space within 20 seconds or less.

(vi)        The system shall be designed to operate within the temperature range likely to be experienced in service.

(vii)       Discharge nozzles shall be so positioned that a uniform distribution of fire extinguishing medium is obtained and the discharge does not endanger personnel engaged on maintenance of machinery or equipment or using the normal access ladders and escapes serving the compartment

(viii)       Safe means shall be provided for the crew to check the quantity of medium in the containers and the pressure therein.

(ix)        The quantity of extinguishing medium for cargo spaces intended solely for the carriage of vehicles which are not carrying any cargo shall be calculated in accordance with the following table.  This quantity shall be based on the gross volume of the protected space.

Table 1

_____________________________________________________________

Halon    Minimum           Maximum

_____________________________________________________________

1301 (BTM)       5 per cent          7 per cent

_____________________________________________________________

1211 (BCF)        5 per cent          5.5 per cent

_____________________________________________________________

The volume of Halon 1301 (BTM) shall be calculated at 0.16 cubic metres per kilogramme and the volume of Halon 1211 (BCF) shall be calculated at 0.14 cubic metres per kilogramme.

(x)        The quantity of extinguishing medium for machinery spaces shall be calculated in accordance with the following Table 2. This quantity shall be based on the gross volume of the space in respect of the minimum concentration and the net volume of the space in respect of the maximum concentration, including the casing.

_____________________________________________________________

Halon    Minimum           Maximum

_____________________________________________________________

1301 (BTM)       4.25 per cent     7 per cent

_____________________________________________________________

1211 (BCF)        4.25 per cent     5.5 per cent

_____________________________________________________________

The volume of Halon 1301 (BTM) shall be calculated at 0.16 cubic metres per kilogramme and the volume of Halon 1211 (BCF) shall be calculated at 0.14 cubic metres per kilogramme.

(c)        Where the medium is Halon 1301 (BTM), the storage containers may be permitted within a protected machinery space other than a pumproom provided that the arrangements comply with the following requirements :

(i)         The containers shall be individually distributed throughout the protected space having regard to the appropriate requirements of sub-para (1)(c).

(ii)         A manually initiated power release, located outside the protected space, shall  be provided.  Duplicate sources of power shall be provided for this release and shall be located outside the protected space and be immediately available except that for machinery spaces, one of the sources of power may be located inside the protected space.

(iii)        The sources of pneumatic and hydraulic pressure and of electrical power shall be monitored for loss of pressure or power as appropriate and electrical circuits essential for the release of the medium from the containers shall be monitored for all fault conditions.  Visual and audible alarms shall be provided to indicate this.  The pneumatic or hydraulic power circuits connecting the containers shall be duplicated.

(iv)        Within the protected space, electrical circuits essential for the release of the medium shall be mineral insolated cable or other equivalent material.  Hydraulic and pneumatic piping systems essential for the release of the medium shall be of steel or other equivalent heat resisting material.

(v)         Each container shall be fitted with an automatic over pressure device which will safely vent the contents of the container into the protected space in the event of over pressure caused by the container being exposed to a fire and in operation or failure of the power.

(vi)        The  arrangements of the containers and the electric circuits and piping essential for the release of the medium shall be such that in the event of damage at any one location in a circuit through fire or explosion, i.e. a single fault concept at least two-thirds of the quantity of medium required for that space in accordance with sub-para  3(b) (ix) or 3(b) (x) can still be discharged at will, having regard to the requirement for uniform distribution of medium throughout the space.  In small compartments, the Chief Surveyor with the Govt.  of India may permit only one or two containers if he is satisfied with the storage and release arrangements.

(vii)       Not more than two discharge nozzles shall be fitted to any pressure container and the maximum quantity of agent in each container shall be adequate, having regard to the requirement for uniform distribution of medium throughout the space.

(viii)       The containers shall be monitored for decrease in pressure due to leakage and discharge.  Visual and audible alarms in the protected area and on the navigation bridge or at the control station hall be provided to indicate this condition, except that for cargo spaces alarms need only be provided on the navigation bridge or the control station.

(d)        Local automatically operated units containing Halon 1301 (BTM) or Halon 1211 (BCF) fitted in enclosed areas of high fire risk within machinery spaces in addition to and independent of any required fixed fire extinguishing system may be accepted provided the units comply with the following requirements:

(i)         The space in which such additional local protection is provided should be on one working level and on the same level as the access.  More than one working level may be permitted subject to an access being provided on each level.

(ii)         The escape arrangements shall be such that escape from anywhere in such protected spaces can be effected in not more than ten seconds.

(iii)        The operation of any unit shall be indicated by visual and audible alarms outside each access into the space and the navigating bridge or at the control station.

(iv)        A notice stating that the space contains one or more automatically operated units and the name of the medium used shall be displayed outside each access to the space.

(v)         The time to discharge the liquid phase of the medium in any local automatically operated unit shall not exceed ten seconds.

(vi)        The arrangements of such units shall be such that release of the medium from any unit does not result in the loss of electrical power or reduction in the maneuverability of the ship.

(vii)       The total quantity of medium provided in such units within a protected space shall be such that the maximum vapour concentration at 200C as specified in sub-para (3) (b) (x) is not exceeded when all such units operate, provided that the concentration may be exceeded where such units are operated together with a fixed system fitted in compliance with sub-para (3) (b).

(viii)       Every such unit shall comply with sub-para (1) (k), (3) (b) (vi), (3) (b) (vii) and (3) (b) (viii).

(e)        Local automatically operated units fitted in machinery spaces over equipment having high fire risk in addition to and independent of any required fixed fire extinguishing system may be accepted provided that they comply with the following requirements:-

(i)         The total quantity of medium provided in such units within the machinery space shall be such that the maximum vapour concentration of 125 per cent of the gross volume of that space is not exceeded when all such units operate simultaneously.

(ii)         Every such unit shall comply with sub-para 1(k), 3(b) (vii) (except that uniform distribution of the medium may not be required), (3) (b) (viii), (3) (d) (iii), (3) (d) (iv), (3) (d) (v), (3) (d) (vi) and (3) (d) (viii).

(4)        Other gas systems.

(a)        Where gas other than carbon dioxide or halogenated hydro-carbon is produced on the ship and is used as in extinguishing medium, it shall be a gaseous product of fuel combustion in which the oxygen content, the carbon monoxide content, the corrosive elements and any solid combustible elements have been reduced to a permissible minimum. Any system using such gas shall afford equivalent protection to that provided by a fixed carbon dioxide system.

(b)        When a system producing inert gas is used to provide extinguishing gas in a fixed fire extinguishing system for cargo spaces, except cargo oil tanks in compliance with these rules, it shall be capable of producing hourly a volume of free gas at least equal to 25 per cent of the gross volume of the largest compartment protected in this way for a period of 72 hours.

(c)        No part of the control storage or generating arrangement of any fixed fire extinguishing system shall be situated forward of the collision bulkhead in any passenger ship.

(5)        Steam system.

In general, the Chief Surveyor with the Government of India, shall not permit the use of steam as a fire extinguishing medium in fixed fire extinguishing systems.  Where the use of steam is permitted by the Chief Surveyor with the Government of India shall be used only in restricted areas as an addition to the required fir extinguishing medium and with the proviso that the boiler or boilers available for applying steam shall have an evaporation of at least 1.0 kg. of steam per hour for each 0.75 m3 of the gross volume of the largest space so protected.  In addition to complying with the foregoing requirements the systems in all respect shall be as determined by and to the satisfaction of the Chief Surveyor with the Government of India.

(6) Fixed gas extinguishing systems shall achieve 85 % CO₂ concentration within 2 minutes; installations shall include visual and audible pre-discharge alarms ≥ 20 seconds before release; remote valve sequencing per FSS Ch. 5 & 2.1.

# SCHEDULE -X

[See rule 10(1) (b), 30(1) (b) and 31(c)]

FIXED HIGH-EXPANSION FOAM FIRE-EXTINGUISHING SYSTEMS IN MACHINERY SPACES

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(1)(a)     Any required fixed high-expansion foam system in machinery spaces shall be capable of rapidly discharging through fixed discharge outlets a quantity of foam sufficient to fill the greatest space to be protected at a rate of at least one m in the depth per minute.  The quantity of foam-forming liquid available shall be sufficient to produce a volume of foam equal to five times the volume of the largest space to be protected.  The expansion ratio of the foam shall not exceed 1,000 to 1.

(b)     The Chief Surveyor with the Government of India may permit alternative arrangements and discharge rates provided that he is satisfied that equivalent protection is achieved.

(2)        Supply ducts for delivering foam air intakes to the foam generator and the number of foam producing units shall in the opinion of the Chief Surveyor with the Government of India, as well provide effective foam production and distribution.

(3)        The arrangement of the foam generator delivery ducting shall be such that a fire in the protected space will not affect the foam generating equipment.

(4)        The foam generator, its sources of power supply, foam-forming liquid and means of controlling the system shall be readily accessible and simple to operate and shall be grouped in as few locations as possible at positions not likely to be cut off by a fire in the protected pace.

SCHEDULE - XI

[See rule 8(2) (a) (b) (c) and 27 (1) (b) and (2)]

FIXED PRESSURE WATER SPRAYING SYSTEMS FOR CARGO SPACES

(1)        Every fixed pressure water spraying system fitted in compliance with these rules shall be provided with a pump piping system, control valves and spraying nozzles.

(2)        The nozzles shall be of an accepted full bore type and shall be arranged so as to secure an effective distribution of water in the spaces which are to be protected.

(3)        The system shall be such as will provide water application at a rate of at least 3.5 litres per square metre per minute for spaces with a deck height not greater than 2.5 metres and at least 5 litres per square metre per minute for space with a deck height greater than 2.5 metres.

(4)        Precautions shall be taken to prevent the nozzles from becoming clogged by impurities in the water.

(5)        The system shall cover the full breadth of the protected space except that in ships where the protected space is sub-divided with longitudinal class "A" divisions forming boundaries of staircase, etc, the breadth of the sections may be reduced accordingly.  In ships of classes I, II, III, IV, V, VIII and IV where the length of the enclosed part of the protected space is 50 metre or over, the system may be divided into sections provided they are at least 20 metres in length.  In ship of other classes the length of a section may be less than 20 metres but shall be not less than 10 metres provided the capacity of the pumps are capable of supplying the two largest adjacent section simultaneously at the application rate referred to in para (3) of this schedule.

(6)        The distribution valves, for the system shall be situated in an easily accessible position adjacent to but outside, the space to be protected which will not readily be cut off by a fire within the space.  Direct access to the distribution valves from the protected spaces and from outside the spaces shall be provided.  Adequate ventilation shall be fitted in the space containing the distribution valves.

(7)        The water supply to the system shall be provided by a pump or pumps, other than the ship's required fire pumps which shall additionally be connected to the system by a lockable non-return valve which will prevent a back flow from the system into the fire main.

(8)        The principal pump or pumps shall be capable of supplying simultaneously at all times at the required pressure all nozzles in the protected spaces, or two adjacent sections if this is less, a quantity of water in accordance with para (2) and (3) of this schedule.

(9)        The principal pump or pumps shall be capable of being brought into operation by remote control which may be manually actuated, from the position at which the distribution valves are situated.

(10)       In ships of classes I, II and III and in ships of class IV of 76 metres or over in length or where the length of the enclosed part of the protected space is 50 metres or over the principal pump or pumps shall be situated in a position reasonably remote from the protected space and from any machinery space of category A.  In ships of other classes the principal pump or pump shall be situated outside the protected space but may be situated within any machinery space.

(11)       In ships of classes I, II and III and in ships of class IV of 76 metres or over in length or where the length of the enclosed part of the protected space is 50 metres or over, if the principal pump or pumps are electrically driven there shall be two sources of power which may be two of the auxiliary generators provided they are independently driven.  If the principal pump or pumps are driven by independent internal combustion type machinery they shall be so situated that a fire in the protected space will not affect the air supply to the machinery and the pump compartment.

(12)       When a fixed pressure water spraying system is provided for the machinery spaces in accordance with schedule XII of these rules the pump required for that system may also be used for the purpose of complying with this schedule.

(13)       The sea suction of the pump shall be so arranged that when the ship is afloat, it will not be necessary to shut off the supply of sea water to the pump for any purpose other than the inspection or repair of the pump.

(14)       The pump suction and discharge valves and any other valves requiring to be operated to bring the pump into operation shall be locked open or be openable from any control position of the system.  A pressure gauge shall be provided at such control positions to show when water is available.

(15)       A waste valve with a short open ended pipe shall be fitted between the pump discharge and section control valves for testing purposes.

(16)       The pipes of the system shall be solid drawn or welded steel or equivalent and they shall be hydraulically tested by the manufactures to twice the working pressure but not less than 20 bar (2N/mm2) and be galvanized internally in per cent corrosion.

(17)       Fittings such as self-aligning swivel joints and flexible pipe situated within the protected space shall not be readily rendered ineffective by heat and where such fittings are used at least one spare of each type fitted shall be carried.

# SCHEDULE XII

[See rules 10(1) (b), 30(1) (b) and 31(c)]

FIXED PRESSURE WATER SPRAYING SYSTEMS FOR MACHINERY SPACES AND CARGO PUMP ROOMS.

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(1)        Every fixed pressure water spraying systems fitted in compliance with these rules shall be provided of approved type and with a pump, piping system, control valves and spraying nozzles.  For machinery space protection the pump shall not be used for any other purpose except that the Chief Surveyor with the Govt. of India may permit the pump to be used for supplying cargo pump room of cargo space water spraying systems where such systems are permitted.  For cargo pump room protection the water supply may be from the ship's main fire pumps provided such pumps comply with the requirements of this schedule.

(2)        The spraying nozzles shall be of such a type sufficient in number and so arranged as to ensure an effective average distribution of water in accordance with the following table.

| Protected Area | Application Rate Litres Per sq. meter/min. |
| --- | --- |
| Boiler fronts or roof firing areas, oil fuel units centrifugal separators (not only water separators), oil fuel purifiers and clarifiers. Hot oil fuel pipes near exhaust pipes or similar heated surface on main or auxiliary diesel engines. Tank top areas and oil tanks not forming part of the ship's structure Cargo pump rooms. | 20 10 5 10 |

(3)        Spraying nozzles shall be fitted above bilges, tank tops and other areas over which oil fuel is liable to spread and above other main fire hazards in the spaces to be protected.

(4)        The water spraying system may be divided into sections and shall be controlled from distribution manifolds the valves of which shall be capable of being operated from easily assessible positions outside the spaces to be protected and which will not be readily cut off by an outbreak of fire within the protected space.

(5)        The water spraying system shall be kept charged at the necessary pressure and the pump supplying the water for the system shall be automatically put into action by a pressure drop in the system.

(6)        The pump may be driven by independent internal combustion type machinery but if it is dependent upon power being supplied from the emergency generator fitted in compliance with the Merchant Shipping (Passenger Ship Construction) rules, 1981 or the Merchant Shipping (Cargo Ship Construction and Survey) Rules, 1988 the generator shall be arranged to start automatically in case of main power failure so that power for the pump is immediately available. When the pump is driven by independent internal combustion type machinery it shall be so situated that a fire in the protected space will not affect the air supply to the machinery and the pump compartment.

(7)        The pump shall be capable of supplying water at the necessary pressure simultaneously to all sections of the water spraying system in any one compartment to be protected.  The pump and its controls shall be installed outside the space or spaces to be protected.  it shall not be possible for a fire in the space or spaces protected by the water spraying system to put the system out of action.

(8)        Means shall be provided which will prevent nozzles from becoming closed by impurities in the water or corrosion of piping, nozzles, valves and pump.

(9)        No part of the water spraying system shall be situated forward of the collision bulkhead in any passenger ship.

(10)       Operating instructions in clear and permanent lettering shall be affixed to every water spraying system or in a position adjacent thereto.

# SCHEDULE XIII

[See Rule 48(1)]

Fixed Deck Foam System

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(1)        The arrangements for providing foam shall be capable of delivering foam to the entire cargo tanks deck area as well as into any cargo tank, the deck of which has been ruptured.

(2)        The deck foam system shall be capable of simple and rapid operation. The main control station for the system shall be suitable located outside the cargo area adjacent to the accommodation paces and readily accessible and operable in the event of fire in the areas protected.

(3)        The rate of supply of foam solution (that is, the mixture of foam concentrate and water before expansion) shall be not less than the following whichever is the greatest:

(a)        0.6 litre per minute per square metre of cargo tanks deck area, where cargo tanks deck area means the maximum breadth of the ship times the total longitudinal extent of the cargo tank spaces.

(a)     6 litres per minute per square metre of the horizontal sectional area of the single tank having the largest such area; or

(b)        6 litres per minute per square metre of the area protected by the largest monitor, such area being entirely forward of the monitor, but not less than 1, 250 litres per minute.

(4)        Sufficient foam concentrate shall be supplied to ensure atleast 20 minutes of foam generation in ship fitted with an inert gas system complying with Schedule XIV to these Regulations or 30 minutes of foam generation in ships not fitted with an inert gas by system when using the solution rates stipulated in para (3) of this Schedule.  The foam expansion ratio (that is, the ratio of the volume of foam produced to the volume of the mixture of foam concentrate and water before expansion) shall not generally exceed 12 to 1.

(5)        Foam from the fixed system shall be supplied by means of monitors and foam applicators.  At least 50 per cent of the foam solution rate required in sub-paras (a) and (b) of para (3) of this Schedule shall be delivered from each monitor.  On tankers of less than 4,000 tonnes deadweight, applicators may be substituted for an installation of monitors.  In such a case the capacity of each applicator shall be at least 25 per cent of the foam solution rate required in sub-para (a) or (b) of para (3) of this Schedule.

(6)(a)     The number and position of monitors shall be such as to comply with para (1) of this Schedule.  The capacity of any monitor shall be at least 3 litres per minute of foam solution per square metre or deck area protected by that monitor, such area being entirely forward of the monitor.  such capacity shall be not less than 1,250 litres per minute.

(b)     The distance from the monitor to the farthest extremely of the protected area forward of that monitor shall not be more than 75 per cent of the monitor throw in still air conditions.

(7)        A monitor and hose connection for a foam applicator shall be situated both port and starboard at the front of the poop or accommodation spaces facing the cargo tanks deck.  On tankers of a deadweight of less than 4,000 tonnes not fitted with monitors a hose connection for a foam applicator shall be situated both port and starboard at the front of the poop or accommodation spaces facing the cargo tanks deck.

(8)        The capacity of any applicator shall be not less than 400 litres per minute and the applicator throw in still air conditions shall be not less than 15 metres.  The number of foam applicators provided in accordance with the requirements of para (5) of this Schedule shall be not less than four.  The number and disposition of foam main outlets shall be such that foam from at least two applicators can be directed on to any part of the cargo tank deck area.

(9)        Valves shall be provided in the foam main, and in the fire main when this is an integral part of the deck foam system, immediately forward of any monitor position to isolate damaged sections of those mains.

(10)       Operation of a deck foam system at its required output shall permit the simultaneous use of the minimum required number of jets of water at the required pressure from the fire main.

# SCHEDULE XIV

[See Rules 48(2), 48(5)(a) and 49(2)]

Inert Gas Systems

This Schedule shall, to the extent applicable, be read in conformity with the provisions of the International Code for Fire Safety Systems (FSS Code), as amended.

(1)        Every inert gas system provided in accordance with these rules shall be designed, constructed and tested to the satisfaction of the Chief Surveyor with the Govt. of India.

(2)        The system shall be capable of :

(a)        inert’ng empty cargo tanks including slop tanks by reducing the oxygen content of the atmosphere in each tank to a level at which combustion cannot be supported;

(b)        maintaining the atmosphere in any part of any cargo tank or slop tank at an oxygen content not exceeding 8 per cent by volume and at a positive pressure at all times both in port and at sea except when it is necessary for such a tank to be gas free;

(c)        eliminating the need for air to enter tank during normal operations except when it is necessary for such tank to be gas free;

(d)        purging empty cargo tanks including slop tanks or hydrocarbon gas, so that subsequent gas freeing operations will at no time create a      atmosphere within the tank.

(3)(a)     The system shall be capable of delivering mert gas to the cargo tanks and stop tanks at a rate of at least 125 per cent of the maximum rate of discharge capacity of the ship, expressed as a volume ;

(b)     the system shall be capable of delivering merit gas with an oxygen content or not more than 5 per cent by volume in the inert gas supply main to the cargo tanks and stop tanks at any required rate of flow.

(4)        The inert gas supply may be treated flue gas from the main or auxiliary boilers, from one or more separate gas generators or other sources or from any combination thereof. Director General of Shipping may approve systems using inert gases other than true gas, provided he is satisfied that an equivalent standard of safety I achieved.  Systems using stored carbon dioxide shall not be permitted unless the Chief Surveyor with the Govt. of India is satisfied that the risk of ignition from generation of state electricity by the system itself is minimized.

(5)        Flue gas isolating valves shall be fitted in the inert gas supply means between the boiler uptakes and flue gas scrubber.  These valves shall be provided with indicators to show whether they are open or shut, and precautions shall be taken to maintain them gas-tight and keep the seating clear of soot.  Arrangements shall be made so that boiler soot blowers cannot be operated when the corresponding flue gas valves open.

(6)(a)     A flue gas scrubber shall be fitted which will effectively cool the volume of gas specified in para (3) of this Schedule and remove solids and sulphur combustion products.  The cooling water arrangements shall be such that an adequate supply of water will always be available without interfering with any essential services on the ship.  Provisions shall also be made for an alternative supply of cooling water;

(b)     Filters or equivalent devices shall be fitted to minimize the amount of water carried over to the inert gas blowers;

(c)     The scrubber shall be located aft of all cargo tanks, slop tanks, cargo pump rooms and cofferdams separating these spaces from machinery spaces of Category A.(7)(a)     Atleast two blowers shall be fitted which together shall be capable of delivering to the cargo tanks and slop tanks, at least the volume of gas required by para (3) of this Schedule.  In a system provided with a gas generator, the Chief Surveyor with the Govt. of India may permit only one blower if that system is capable of delivering the total volume of gas required by para (3) to the protected cargo tanks, provided that sufficient spares for the blower and its prime mover are carried on board to enable any failure of the blower and its prime mover to be rectified by the ship's crew.

(b)     Two fuel oil pumps shall be fitted to the inert gas generator, Chief Surveyor with the Govt. of India may permit only one fuel oil pump on condition that  sufficient spares for the fuel oil pump and its prime mover are carried on board to enable any failure of the fuel oil pump and its prime mover to be rectified by the ship's crew.

(c)     The inert gas system be so designed that the maximum pressure which it can exert on any cargo tank will not exceed the test pressure of any cargo tank.  Suitable shut-off arrangements shall be provided on the suction and discharge connexions of each blower.  Arrangements shall be provided to enable the functioning of the inert gas plant to be stabilized before commencing cargo discharge.  If the blowers are to be used for gas freeing, their inlets shall be provided with blanking arrangements.

(d)     The blowers shall be located aft of all cargo tanks, cargo pump rooms and conterdams separating these spaces from machinery spaces of Category A.

(8)(a)     The design and location of scrubber and blowers with relevant piping and fittings shall be such as to prevent fire gas leakages into enclosed spaces.

(b)     To permit safe maintenance, an additional water seal or other effective means of preventing flue gas leakage shall be fitted between the flue gas isolating valves and scrubber or incorporated in the gas entry to the scrubber.

(9)(a)     A gas regulating valve shall be fitted in the inert gas supply main.  This valve shall be automatically controlled to close as required in para (19)(c) and 19(d) of this Schedule.  It shall also be capable of automatically regulating the flow of inert gas to the cargo tanks unless means are provided to automatically control the speed of the inert gas blowers required in para (7) of this Schedule.

(b)     The valve referred to in sub-para (a) of this para shall be located at the forward bulkhead of the most forward gas safe space through which the inert gas supply main passes.

(10)(a)At least two non-return devices, one of which shall be a water seal, shall be fitted in the inert gas supply main, in order to prevent the return of hydrocarbon vapour to machinery spaces uptakes or to any gas safe spaces under all normal conditions of trim; 1st  and motion of the ship.  They shall be located between the automatic valve required by para (9) of this Schedule and the aftermost connection to any cargo tank or cargo pipeline.

(b)     The devices referred to in this para shall be located in the cargo area on deck.

(c)     The water seal referred to in sub-para (a) of this para shall be capable of being supplied by two separate pumps, each of which shall be capable of maintaining an adequate supply at all times.

(d)     The arrangement of the seal and its associated provisions shall be such that it will prevent back-flow of hydrocarbon vapours and will ensure the proper functioning of the seal under operating conditions.

(e)     Provision shall be made to ensure that the water seal is protected against freezing, in such a way that the integrity of the seal is not impaired by overheating.

(f)         A water loop or other arrangement approved by Director General of Shipping shall also be fitted in all associated water supply and dry piping and all venting or pressure sensing piping leading to gas safe spaces.  Means shall be provided to prevent such loops from being emptied by vacuum.

(g)        The deck water seal and all loop arrangements shall be capable of preventing return of hydrocarbon vapours at a pressure equal to the test pressure of the cargo tanks.

(h)        The second non-return device mentioned in sub-para (a) of this paragraph shall be a non-return valve or equivalent capable of preventing the return of vapours or liquids or both fitted forward of the deck water seal required by sub-para (a) of this para.  It shall be provided with either positive means of closure or an additional valve having such means of closure located forward of the non-return valve to isolate the deck water seal from the inert gas main to the cargo tanks and slop tanks.

(i)         As an additional safeguard against the possible leakage of hydrocarbon liquids or vapours back from the deck main, means shall be provided to permit the section of the line between the valve having positive means of closure referred to in sub-para (h) of this para, and the valve referred to in para (9) of this Schedule to be vented in a safe manner when the first of these valves is closed.

11(a)     The inert gas main may be divided into two or more branches forward of the non-return devices required by para (10) of this schedule.

(b)(i)      The inert gas supply main shall be fitted with branch piping leading to each cargo tank and slop tank.  Branch piping for inert gas shall be fitted with either stop valves or equivalent means of control for isolating each tank.  Where stop valves are fitted they shall be provided with locking arrangements, which shall be under the control of a responsible ship's officer.

(ii)      In combination carriers, the arrangements to isolate the slop tanks containing oil or oil residues from other tanks shall consist of blank flanges which will remain in position at all times when cargoes other then oil are being carried except as provided for in the relevant section of the Guidelines on Inert Gas Systems.

(c)        Means shall be provided to protect cargo tanks and stop tanks against effect of over pressure or vacuum caused by thermal variations when such tanks are isolated from the inert gas main.

(d)        Piping systems shall be so designed as to prevent the accumulation of cargo or water in the pipelines under all normal conditions.

(12)       The arrangements for the venting of all vapours displaced from the cargo tanks during loading or ballasting shall comply with rule 66 of the Merchant Shipping (Cargo Ship Construction and Survey) Rules, 1988 and shall consist of either one or more mast risers or a number of rigid velocity vents.  The inert gas supply main may be used for such venting.

(13)       The arrangements for inerting, purging or gas freeing of empty tanks as required in para (2) of this Schedule shall be approved and shall be such that the accumulation of hydrocarbon vapours in pockets formed by the internal structural members in a tank is minimised and that :

(a)        on individual cargo tanks or slop tanks the gas outlet pipe, if fitted, shall be positioned as far as practicable from the inert gas/air inlet and in accordance with rule 66 of the Merchant Shipping (Cargo Ship Construction and Survey) Rules 1988.   The inlet of such outlet pips may be located at either deck level or at not more than 1 metre above the bottom of the tank;

(b)        the cross sectional area of such a gas outlet pipe referred to in sub-para (1) of this para shall be such that an exit velocity of at least 20 metres per second can be maintained when any three tanks are being simultaneously supplied with inert gas.  Their outlets shall extend not less than 2 metres above deck level;

(c)        each gas outlet referred to in sub-para (b) of this para shall be fitted with suitable blanking arrangements;

(d)(i)      if a connection is fitted between the inert gas supply main and the cargo piping system arrangements shall be made to ensure an effective isolation having regard to the high pressure difference which may exist between the systems.  This shall consist of two shut off valves with an arrangements to vent the space between the valves in a safe manner or an arrangement consisting or a spoolpiece with associated blanks.

(ii)      the valve separating the inert gas supply main from the cargo main shall be a non-return valve with a positive means of closure.

(14)(a)      One or more pressure-vacuum breaking devices shall be provided to prevent the cargo tanks from being subject to :

(i)         a positive pressure in excess of the test pressure of the cargo tank if the cargo were to be loaded at the maximum rated capacity and all other outlets were left shut; and

(ii)         a negative pressure in excess of 700 milimetres water gauge if cargo were to be discharged at the maximum rated capacity of the cargo pumps and the inert gas blower were to fail.  Such devices shall be installed on the inert gas main unless they are installed in the venting system required by rule 66 of the Merchant Shipping (Cargo Ship Construction and Survey) Rules 1988 or on individual cargo tanks.

(b)     The location and design of the devices referred to in sub-para (a) of this para shall be in accordance with rule 66 of the Merchant Shipping (Cargo Ship Construction and Survey) Rules, 1988.

(15)       Means shall be provided for continuously indicating the temperature and pressure of the inert gas at the discharge side of the gas blowers, whenever those gas blowers are operating.

(16)(a)Instrumentation shall be fitted for continuously indicating and permanently recording when inert gas is being supplied.

(i)         the pressure of the inert gas supply main forward of the non-return devices required by sub-para (a) of para (10) of this Schedule; and

(ii)         the oxygen content of the inert gas in the inert gas supply main on the discharge side of the gas blowers

(b)     The devices referred to in sub-para 9a) of this para shall be placed in the cargo control room where provided.  Where no cargo control room is provided they shall be placed in a position easily accessible to the officer in charge of cargo operations.

(c)      In addition, meters shall be fitted :

(i)         in the navigating bridge, to indicate at all times the pressure referred to in sub-para (a)(i) of this para and the pressure in the slop tanks of combination carriers, whenever those tanks are isolated from the inert gas supply main; and

(ii)         in the machinery control room or in the machinery space, to indicate the oxygen content referred to in sub-para (a) (ii) of this para.

(17)       Portable instruments for measuring oxygen and flammable vapour concentration shall be provided.  In addition, suitable arrangements shall be made on each cargo tank and slop tank such that the condition of the tank atmosphere can be determined using these portable instruments.

(18)       Suitable means shall be provided for the zero and span calibration of both fixed and portable gas concentration measurement instruments, referred to in para (16) and (17) of this Schedule.

(19)(a)   Audible and visual alarms shall be provided to indicate:

(i)         low water pressure or low water flow rate to the flue gas scrubber referred to in sub-para (6)(a) of this Schedule;

(ii)         high water level in the flue gas scrubber referred to in sub-para (6)(a) of this Schedule;

(iii)        high gas temperature referred to in para (15) of this Schedule;

(iv)        failure of the inert gas blowers referred to in sub-para (7)(a) of this Schedule;

(v)         Oxygen content in excess of 8 per cent volume referred to in sub-para (16)((a)(ii) of this Schedule;

(vi)        failure of the power supply to the automatic control system for the gas regulating valve and to the indicating devices referred to in para (9) and sub-para (16)(a) respectively of this Schedule;

(vii)       low water level in the water seal referred to in sub-para (10)(a) of this Schedule;

(viii)       gas pressure less than 100 millimetres water gauge as referred to in sub-para (16)(a)(i) of this Schedule; the alarm arrangement for this gas pressure shall be such as to ensure that the pressure in slop tanks in combination carriers can be monitored at all times; and

(ix)        high gas pressure referred to in sub-para (16)(a)(i) of this Schedule.

(b)        In the system with gas generators, audible and visual alarms shall be provided in accordance with sub para 19(a)(i), 19(a)(iii), 19(a)(v) and 19(a)(ix) of this para and additional alarms to indicate:

(i)         insufficient fuel oil supply ;

(ii)         failure of the power supply to the generator;

(iii)        failure of the power supply to the automatic control system for the generator.

(c)        Automatic shut down of the inert gas blowers and gas regulating valve shall be arranged on predetermined limit being reached in respect of sub-para (a)(i), (a) (ii) and (a) (iii) of this para.

(d)        Automatic shut down of the gas blowers and gas regulating valve shall be arranged so as to take account of failure of the inert gas blowers referred to in para (7) of this Schedule.

(e)        In relation to sub-para (a)(v) of this para, when the oxygen content of the inert gas exceeds 8 per cent, immediately action shall be taken to reduce the oxygen level.  Unless the quality of the gas improves, all in-tank operations shall be suspended so as to avoid air being drawn into the tanks and the isolation valve referred to in sub-para 10(h) of this Schedule shall be closed.

(f)         The alarms required in sub-para (a)(v), (a) (vi), and (a) (viii) of this para shall be fitted in the machinery space and cargo control room, where provided, but in any event in such a position that they are immediately received by responsible members of the crew.

(g)        In relation to sub-para (a)(vii) of this para the Chief Surveyor with the Govt. of India shall be satisfied as to the maintenance of an adequate reserve of water at all times and the integrity of the arrangements to permit the automatic formation of the water seal when the gas flow ceases.  The audible and visual alarm on the low level of water in the water seal shall operate when the inert gas is not being supplied.

(h)        An audible alarm system, independent of that required in sub-para (a)(viii) of this para, or automatic shut down of cargo pumps shall be provided to operate on predetermined limits of low pressure in the inert gas main being reached.

(20)       A detailed instruction manual shall be provided on board by the owner and it shall cover the operational safety and maintenance requirements and occupational health hazards relevant to the inert gas system and its application to the cargo tank system.  The manual shall include guidance on procedures to be followed in the event of a fault or failure of the inert gas system as detailed in the Guidelines for Inert Gas System.

# Schedule XV

See Rule (XX)

[Title of Schedule]

Sprinkler System Zoning

Automatic sprinkler systems shall be divided into sections not exceeding 200 sprinkler heads, with test valves and pressure gauges; design verification shall follow MSC.265(84).

Special Spaces (Helidecks, Ro-Ro Decks, Inert Gas Systems)

Helideck fire-fighting systems shall deliver foam at ≥ 5 L/m²/min for 2 minutes through nozzles ensuring ≥ 1 jet covering the landing area. Ro-Ro deck monitors shall discharge ≥ 1,250 L/min. Inert gas systems shall provide ≥ 95 % CO₂ purity with dual pressure relief valves and automatic shutdown controls.

Ventilation Safety and Smoke Extraction

Ventilation fans shall automatically shut down upon fire alarm activation; exhaust fans shall start automatically in smoke extraction mode for affected zones. System capacity ≥ 10 air changes per hour in machinery spaces.